## Existing Generators
Technical parameters and operating costs (costs in 2014-15 $)
Station | Unit | Region | Zone | Generation Type | Fuel Type | Fuel Cost Profile | First Run | Min Gen (% of nameplate capacity) | Minimum On Time (Hours) | Minimum Off Time (Hours) | No Load Fuel Consumption (% of Full Load Fuel Consumption) | Auxiliary load (% of nameplate capacity) | Hot Day Derate factor (% of nameplate capacity) | Ramp Up Rate (MW/h) - for start up | Ramp Up Rate (MW/h) - when running normally | Ramp Down Rate (MW/h) - for shut down | Ramp Down Rate (MW/h) - when running normally | Thermal Efficiency (%, HHV sent-out) | Pumping Efficiency (GWh pumped per GWh generated) - within 24 hours | Pumping Efficiency ( GWh pumped per GWh generated) - annual | Maintenance (days/yr) | Fixed Op Cost ($/MW/year) | Variable Op Cost ($/MWh sent-out) | No Load Costs ($/MW, 2014-15 $) | No Load Recurring Cost ($/MW/year) | Cold Start-up Notificatio nTime (Hr) | Warm Start-up Notificatio nTime (Hr) | Hot Start-up Notificatio nTime (Hr) | Cold Start-up Costs ($/MW) | Warm Start-up Costs ($/MW) | Hot Start-up Costs ($/MW) | Retirement/Rehabilitation ($/MW) | Full Forced Outage Rate (% of time) | Partial Forced Outage Rate (% of time) | Partial Derating (% of namplate capacity) | Equivalent Forced Outage Rate (% of time) | Available To Partial | Available to Unavailable | Partial to Available | Partial to Unavailable | Unavailable to Available | Unavailable to Partial | Scope 1 emission factors (kg CO2-e/GJ of fuel) | Scope 3 emission factors (kg CO2-e/GJ of fuel)
Tallawarra | Tallawarra | NSW | NCEN | CCGT | Natural gas | Tallawarra | 2009 | 0 | 4 | 4 | 30 | 3 | 1.1905 | 180 | 360 | 180 | 360 | 50 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 51.2839 | 13.5
Condamine | Condamine | QLD | SWQ | CCGT | Natural gas | Condamine | 2009 | 0 | 4 | 4 | 30 | 3 | 0 | 170 | 180 | 170 | 180 | 48 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 62.4503 | 7.6
Condamine | Condamine GT2 | QLD | SWQ | CCGT | Natural gas | Condamine | 2009 | 0 | 4 | 4 | 30 | 3 | 0 | 170 | 180 | 170 | 180 | 48 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 62.4503 | 7.6
Condamine | Condamine ST | QLD | SWQ | CCGT | Natural gas | Condamine | 2009 | 0 | 4 | 4 | 30 | 3 | 0 | 170 | 180 | 170 | 180 | 48 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 62.4503 | 7.6
Darling Downs | DDPS1_GT1 | QLD | SWQ | CCGT | Natural gas | Darling Downs | 2010 | 0 | 4 | 4 | 30 | 6 | 7.9365 | 490 | 380 | 490 | 380 | 46 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 57.1179 | 7.6
Darling Downs | DDPS1_GT2 | QLD | SWQ | CCGT | Natural gas | Darling Downs | 2010 | 0 | 4 | 4 | 30 | 6 | 7.9365 | 490 | 380 | 490 | 380 | 46 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 57.1179 | 7.6
Darling Downs | DDPS1_GT3 | QLD | SWQ | CCGT | Natural gas | Darling Downs | 2010 | 0 | 4 | 4 | 30 | 6 | 7.9365 | 490 | 380 | 490 | 380 | 46 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 57.1179 | 7.6
Darling Downs | DDPS1_ST | QLD | SWQ | CCGT | Natural gas | Darling Downs | 2010 | 0 | 4 | 4 | 30 | 6 | 7.9365 | 490 | 380 | 490 | 380 | 46 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 57.1179 | 7.6
Swanbank E | SWAN_E | QLD | SEQ | CCGT | Natural gas | Swanbank E | 2002 | 0 | 4 | 4 | 30 | 3 | 0 | 620 | 640 | 640 | 640 | 47 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 51.8863 | 7.6
Townsville | TOWNSV1 | QLD | NQ | CCGT | Natural gas | Townsville | 2005 | 0 | 4 | 4 | 30 | 3 | 3.7037 | 770 | 340 | 770 | 340 | 46 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 56.0896 | 7.6
Townsville | TOWNSV2 | QLD | NQ | CCGT | Natural gas | Townsville | 2005 | 0 | 4 | 4 | 30 | 3 | 3.7037 | 770 | 340 | 770 | 340 | 46 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 56.0896 | 7.6
Osborne | OsborneGT | SA | ADE | CCGT | Natural gas | Osborne | 1998 | 0 | 4 | 4 | 30 | 5 | 2.7778 | 170 | 160 | 170 | 160 | 42 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 61.7419 | 10.2
Osborne | OsborneST | SA | ADE | CCGT | Natural gas | Osborne | 1998 | 0 | 4 | 4 | 30 | 5 | 2.7778 | 170 | 160 | 170 | 160 | 42 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 61.7419 | 10.2
Pelican Point | PPCCGTGT1 | SA | ADE | CCGT | Natural gas | Pelican Point | 2000 | 0 | 4 | 4 | 30 | 2 | 5.4852 | 600 | 600 | 600 | 600 | 48 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 54.0461 | 10.2
Pelican Point | PPCCGTGT2 | SA | ADE | CCGT | Natural gas | Pelican Point | 2000 | 0 | 4 | 4 | 30 | 2 | 5.4852 | 600 | 600 | 600 | 600 | 48 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 54.0461 | 10.2
Pelican Point | PPCCGTST | SA | ADE | CCGT | Natural gas | Pelican Point | 2000 | 0 | 4 | 4 | 30 | 2 | 5.4852 | 600 | 600 | 600 | 600 | 48 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 54.0461 | 10.2
Tamar Valley CCGT | Tamar CCGT | TAS | TAS | CCGT | Natural gas | Tamar Valley CCGT | 2010 | 0 | 4 | 4 | 30 | 3 | 0 | 430 | 110 | 430 | 540 | 48 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 56.4096 | 0
Smithfield | SITHE01 | NSW | NCEN | Cogen | Natural gas | Smithfield | 1997 | 0 | NA | NA | 30 | 5 | 5.2077 | 60 | 70 | 180 | 180 | 41 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 57.6557 | 13.5
Smithfield | SITHE02 | NSW | NCEN | Cogen | Natural gas | Smithfield | 1997 | 0 | NA | NA | 30 | 5 | 5.2077 | 60 | 70 | 180 | 180 | 41 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 57.6557 | 13.5
Smithfield | SITHE03 | NSW | NCEN | Cogen | Natural gas | Smithfield | 1997 | 0 | NA | NA | 30 | 5 | 5.2077 | 60 | 70 | 180 | 180 | 41 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 57.6557 | 13.5
Smithfield | SITHE04 | NSW | NCEN | Cogen | Natural gas | Smithfield | 1997 | 0 | NA | NA | 30 | 5 | 5.2077 | 60 | 70 | 180 | 180 | 41 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 57.6557 | 13.5
Yarwun CoGen | Yarwun CoGen | QLD | CQ | CoGen | Natural gas | Yarwun | 2010 | 0 | NA | NA | 30 | 2 | 0 | 600 | 600 | 600 | 600 | 34 |  |  | 20 | 10000 | 7 | 800 | 300 | 15 | 3 | 1 | 25 | 15 | 5 | 10000 | 2 | 1 | 50 | 2.5 | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 51.3 | 7.6
Blowering | BLOWRNG | NSW | SWNSW | Hydro | Hydro | Hydro | 1969 | 6 | 1 | 1 | N/A | 1 | 0 | 120 | 120 | 120 | 120 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Guthega | GUTHEGA1 | NSW | CAN | Hydro | Hydro | Hydro | 1955 | 35 | 1 | 1 | N/A | 1 | 0 | 580 | 590 | 600 | 600 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Guthega | GUTHEGA2 | NSW | CAN | Hydro | Hydro | Hydro | 1955 | 35 | 1 | 1 | N/A | 1 | 0 | 580 | 590 | 600 | 600 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Hume (NSW) | HUMENSW | NSW | SWNSW | Hydro | Hydro | Hydro | 1957 | 14 | 1 | 1 | N/A | 1 | 0 | 180 | 180 | 180 | 180 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 2 | 1 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Shoalhaven | SHGEN01 | NSW | NCEN | Hydro | Hydro | Hydro | 1977 | 0 | 1 | 1 | N/A | 1 | 0 | 600 | 600 | 600 | 600 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Shoalhaven | SHGEN02 | NSW | NCEN | Hydro | Hydro | Hydro | 1977 | 0 | 1 | 1 | N/A | 1 | 0 | 600 | 600 | 600 | 600 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Shoalhaven | SHGEN03 | NSW | NCEN | Hydro | Hydro | Hydro | 1977 | 0 | 1 | 1 | N/A | 1 | 0 | 600 | 600 | 600 | 600 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Shoalhaven | SHGEN04 | NSW | NCEN | Hydro | Hydro | Hydro | 1977 | 0 | 1 | 1 | N/A | 1 | 0 | 600 | 600 | 600 | 600 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 1 | TUMUT1_01 | NSW | SWNSW | Hydro | Hydro | Hydro | 1959 | 0 | 1 | 1 | N/A | 1 | 0 | 7630 | 7790 | 1840 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 1 | TUMUT1_02 | NSW | SWNSW | Hydro | Hydro | Hydro | 1959 | 0 | 1 | 1 | N/A | 1 | 0 | 7630 | 7790 | 1840 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 1 | TUMUT1_03 | NSW | SWNSW | Hydro | Hydro | Hydro | 1959 | 0 | 1 | 1 | N/A | 1 | 0 | 7630 | 7790 | 1840 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 1 | TUMUT1_04 | NSW | SWNSW | Hydro | Hydro | Hydro | 1959 | 0 | 1 | 1 | N/A | 1 | 0 | 7630 | 7790 | 1840 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 2 | TUMUT2_01 | NSW | SWNSW | Hydro | Hydro | Hydro | 1962 | 0 | 1 | 1 | N/A | 1 | 0 | 7630 | 7790 | 1840 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 2 | TUMUT2_02 | NSW | SWNSW | Hydro | Hydro | Hydro | 1962 | 0 | 1 | 1 | N/A | 1 | 0 | 7630 | 7790 | 1840 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 2 | TUMUT2_03 | NSW | SWNSW | Hydro | Hydro | Hydro | 1962 | 0 | 1 | 1 | N/A | 1 | 0 | 7630 | 7790 | 1840 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 2 | TUMUT2_04 | NSW | SWNSW | Hydro | Hydro | Hydro | 1962 | 0 | 1 | 1 | N/A | 1 | 0 | 7630 | 7790 | 1840 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 3 | TUMUT3_01 | NSW | SWNSW | Hydro | Hydro | Hydro | 1973 | 0 | 1 | 1 | N/A | 1 | 0 | 12000 | 12000 | 2890 | 2120 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 3 | TUMUT3_02 | NSW | SWNSW | Hydro | Hydro | Hydro | 1973 | 0 | 1 | 1 | N/A | 1 | 0 | 12000 | 12000 | 2890 | 2120 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 3 | TUMUT3_03 | NSW | SWNSW | Hydro | Hydro | Hydro | 1973 | 0 | 1 | 1 | N/A | 1 | 0 | 12000 | 12000 | 2890 | 2120 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 3 | TUMUT3_04 | NSW | SWNSW | Hydro | Hydro | Hydro | 1973 | 0 | 1 | 1 | N/A | 1 | 0 | 12000 | 12000 | 2890 | 2120 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 3 | TUMUT3_05 | NSW | SWNSW | Hydro | Hydro | Hydro | 1973 | 0 | 1 | 1 | N/A | 1 | 0 | 12000 | 12000 | 2890 | 2120 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tumut 3 | TUMUT3_06 | NSW | SWNSW | Hydro | Hydro | Hydro | 1973 | 0 | 1 | 1 | N/A | 1 | 0 | 12000 | 12000 | 2890 | 2120 | 100 | 1.7 | 1.7 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Barron Gorge | BARRON1 | QLD | NQ | Hydro | Hydro | Hydro | 1963 | 0 | 1 | 1 | N/A | 1 | 0 | 180 | 180 | 180 | 180 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 0 | 0 | 0 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Barron Gorge | BARRON2 | QLD | NQ | Hydro | Hydro | Hydro | 1963 | 0 | 1 | 1 | N/A | 1 | 0 | 180 | 180 | 180 | 180 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 0 | 0 | 0 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Kareeya | KAREEYA1 | QLD | NQ | Hydro | Hydro | Hydro | 1958 | 25 | 1 | 1 | N/A | 1 | 0 | 300 | 300 | 120 | 120 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 0 | 0 | 0 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Kareeya | KAREEYA2 | QLD | NQ | Hydro | Hydro | Hydro | 1958 | 25 | 1 | 1 | N/A | 1 | 0 | 300 | 300 | 120 | 120 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 0 | 0 | 0 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Kareeya | KAREEYA3 | QLD | NQ | Hydro | Hydro | Hydro | 1958 | 25 | 1 | 1 | N/A | 1 | 0 | 300 | 300 | 120 | 120 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 0 | 0 | 0 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Kareeya | KAREEYA4 | QLD | NQ | Hydro | Hydro | Hydro | 1958 | 25 | 1 | 1 | N/A | 1 | 0 | 300 | 300 | 120 | 120 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 0 | 0 | 0 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Wivenhoe | W/HOE1 | QLD | SEQ | Hydro | Hydro | Hydro | 1984 | 25 | 1 | 1 | N/A | 1 | 0 | 7200 | 7200 | 7200 | 7200 | 100 | 1.7 | 2 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Wivenhoe | W/HOE2 | QLD | SEQ | Hydro | Hydro | Hydro | 1984 | 25 | 1 | 1 | N/A | 1 | 0 | 7200 | 7200 | 7200 | 7200 | 100 | 1.7 | 2 | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Bastyan | BA131-1 | TAS | TAS | Hydro | Hydro | Hydro | 1983 | 0.07 | 1 | 1 | N/A | 1 | 0 | 740 | 1790 | 740 | 1790 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Cethana | CE131-1 | TAS | TAS | Hydro | Hydro | Hydro | 1971 | 0 | 1 | 1 | N/A | 1 | 0 | 1260 | 1790 | 1260 | 1790 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Devils Gate | DG111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1969 | 8 | 1 | 1 | N/A | 1 | 0 | 1070 | 1790 | 1070 | 1790 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Fisher | FI111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1973 | 0 | 1 | 1 | N/A | 1 | 0 | 440 | 890 | 440 | 890 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Gordon | GO181-1 | TAS | TAS | Hydro | Hydro | Hydro | 1978 | 0 | 1 | 1 | N/A | 1 | 0 | 2890 | 5250 | 2780 | 140 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Gordon | GO182-2 | TAS | TAS | Hydro | Hydro | Hydro | 1978 | 0 | 1 | 1 | N/A | 1 | 0 | 2890 | 5250 | 2780 | 140 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Gordon | GO183-3 | TAS | TAS | Hydro | Hydro | Hydro | 1978 | 0 | 1 | 1 | N/A | 1 | 0 | 2890 | 5250 | 2780 | 140 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
John Butters | JB131-1 | TAS | TAS | Hydro | Hydro | Hydro | 1992 | 0 | 1 | 1 | N/A | 1 | 0 | 1610 | 1730 | 1610 | 1730 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Lake Echo | LE111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1956 | 0 | 1 | 1 | N/A | 1 | 0 | 1000 | 1000 | 1000 | 1000 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Lemonthyme_Wilmot | LM111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1970 | 0 | 1 | 1 | N/A | 1 | 0 | 400 | 1170 | 400 | 1170 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Lemonthyme_Wilmot | WI111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1970 | 0 | 1 | 1 | N/A | 1 | 0 | 400 | 1170 | 400 | 1170 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Liapootah_Wayatinah_Catagunya | CA111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1960 | 0 | 1 | 1 | N/A | 1 | 0 | 940 | 2480 | 940 | 2480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Liapootah_Wayatinah_Catagunya | CA112-2 | TAS | TAS | Hydro | Hydro | Hydro | 1960 | 0 | 1 | 1 | N/A | 1 | 0 | 940 | 2480 | 940 | 2480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Liapootah_Wayatinah_Catagunya | LI111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1960 | 0 | 1 | 1 | N/A | 1 | 0 | 940 | 2480 | 940 | 2480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Liapootah_Wayatinah_Catagunya | LI112-2 | TAS | TAS | Hydro | Hydro | Hydro | 1960 | 0 | 1 | 1 | N/A | 1 | 0 | 940 | 2480 | 940 | 2480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Liapootah_Wayatinah_Catagunya | LI113-3 | TAS | TAS | Hydro | Hydro | Hydro | 1960 | 0 | 1 | 1 | N/A | 1 | 0 | 940 | 2480 | 940 | 2480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Liapootah_Wayatinah_Catagunya | WY111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1960 | 0 | 1 | 1 | N/A | 1 | 0 | 940 | 2480 | 940 | 2480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Liapootah_Wayatinah_Catagunya | WY111-2 | TAS | TAS | Hydro | Hydro | Hydro | 1960 | 0 | 1 | 1 | N/A | 1 | 0 | 940 | 2480 | 940 | 2480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Liapootah_Wayatinah_Catagunya | WY111-3 | TAS | TAS | Hydro | Hydro | Hydro | 1960 | 0 | 1 | 1 | N/A | 1 | 0 | 940 | 2480 | 940 | 2480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Mackintosh | MA131-1 | TAS | TAS | Hydro | Hydro | Hydro | 1982 | 0 | 1 | 1 | N/A | 1 | 0 | 1000 | 1800 | 1000 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Meadowbank | MB111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 290 | 480 | 290 | 480 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Poatina | PO161-1 | TAS | TAS | Hydro | Hydro | Hydro | 1964 | 0 | 1 | 1 | N/A | 1 | 0 | 1210 | 2250 | 1220 | 2260 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Poatina | PO162-2 | TAS | TAS | Hydro | Hydro | Hydro | 1964 | 0 | 1 | 1 | N/A | 1 | 0 | 1210 | 2250 | 1220 | 2260 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Poatina | PO163-3 | TAS | TAS | Hydro | Hydro | Hydro | 1964 | 0 | 1 | 1 | N/A | 1 | 0 | 1210 | 2250 | 1220 | 2260 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Poatina | PO164-4 | TAS | TAS | Hydro | Hydro | Hydro | 1964 | 0 | 1 | 1 | N/A | 1 | 0 | 1210 | 2250 | 1220 | 2260 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Poatina | PO165-5 | TAS | TAS | Hydro | Hydro | Hydro | 1964 | 0 | 1 | 1 | N/A | 1 | 0 | 1210 | 2250 | 1220 | 2260 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Poatina | PO166-6 | TAS | TAS | Hydro | Hydro | Hydro | 1964 | 0 | 1 | 1 | N/A | 1 | 0 | 1210 | 2250 | 1220 | 2260 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Reece | RC131-1 | TAS | TAS | Hydro | Hydro | Hydro | 1986 | 0 | 1 | 1 | N/A | 1 | 0 | 880 | 1800 | 890 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Reece | RC132-2 | TAS | TAS | Hydro | Hydro | Hydro | 1986 | 0 | 1 | 1 | N/A | 1 | 0 | 880 | 1800 | 890 | 1800 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tarraleah | TA111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1938 | 0 | 1 | 1 | N/A | 1 | 0 | 1000 | 1000 | 1000 | 1000 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tarraleah | TA111-2 | TAS | TAS | Hydro | Hydro | Hydro | 1938 | 0 | 1 | 1 | N/A | 1 | 0 | 1000 | 1000 | 1000 | 1000 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tarraleah | TA111-3 | TAS | TAS | Hydro | Hydro | Hydro | 1938 | 0 | 1 | 1 | N/A | 1 | 0 | 1000 | 1000 | 1000 | 1000 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tarraleah | TA112-4 | TAS | TAS | Hydro | Hydro | Hydro | 1938 | 0 | 1 | 1 | N/A | 1 | 0 | 1000 | 1000 | 1000 | 1000 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tarraleah | TA112-5 | TAS | TAS | Hydro | Hydro | Hydro | 1938 | 0 | 1 | 1 | N/A | 1 | 0 | 1000 | 1000 | 1000 | 1000 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tarraleah | TA112-6 | TAS | TAS | Hydro | Hydro | Hydro | 1938 | 0 | 1 | 1 | N/A | 1 | 0 | 1000 | 1000 | 1000 | 1000 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Trevallyn | TR111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1955 | 0 | 1 | 1 | N/A | 1 | 0 | 500 | 1710 | 500 | 1710 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Trevallyn | TR111-2 | TAS | TAS | Hydro | Hydro | Hydro | 1955 | 0 | 1 | 1 | N/A | 1 | 0 | 500 | 1710 | 500 | 1710 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Trevallyn | TR112-3 | TAS | TAS | Hydro | Hydro | Hydro | 1955 | 0 | 1 | 1 | N/A | 1 | 0 | 500 | 1710 | 500 | 1710 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Trevallyn | TR112-4 | TAS | TAS | Hydro | Hydro | Hydro | 1955 | 0 | 1 | 1 | N/A | 1 | 0 | 500 | 1710 | 500 | 1710 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tribute | TT131-1 | TAS | TAS | Hydro | Hydro | Hydro | 1994 | 0 | 1 | 1 | N/A | 1 | 0 | 800 | 1780 | 800 | 1780 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tungatinah | TU111-1 | TAS | TAS | Hydro | Hydro | Hydro | 1953 | 0 | 1 | 1 | N/A | 1 | 0 | 590 | 1930 | 590 | 1930 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tungatinah | TU112-2 | TAS | TAS | Hydro | Hydro | Hydro | 1953 | 0 | 1 | 1 | N/A | 1 | 0 | 590 | 1930 | 590 | 1930 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tungatinah | TU113-3 | TAS | TAS | Hydro | Hydro | Hydro | 1953 | 0 | 1 | 1 | N/A | 1 | 0 | 590 | 1930 | 590 | 1930 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tungatinah | TU114-4 | TAS | TAS | Hydro | Hydro | Hydro | 1953 | 0 | 1 | 1 | N/A | 1 | 0 | 590 | 1930 | 590 | 1930 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Tungatinah | TU115-5 | TAS | TAS | Hydro | Hydro | Hydro | 1953 | 0 | 1 | 1 | N/A | 1 | 0 | 590 | 1930 | 590 | 1930 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Dartmouth | DARTM1 | VIC | NVIC | Hydro | Hydro | Hydro | 1960 | 12 | 1 | 1 | N/A | 1 | 0 | 3270 | 3120 | 3270 | 3010 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Eildon | EILDON1 | VIC | NVIC | Hydro | Hydro | Hydro | 1957 | 30 | 1 | 1 | N/A | 1 | 0 | 900 | 900 | 900 | 900 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Eildon | EILDON2 | VIC | NVIC | Hydro | Hydro | Hydro | 1957 | 30 | 1 | 1 | N/A | 1 | 0 | 900 | 900 | 900 | 900 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Hume (VIC) | HUMEV | VIC | NVIC | Hydro | Hydro | Hydro | 1957 | 14 | 1 | 1 | N/A | 1 | 0 | 180 | 180 | 180 | 180 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 2 | 1 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
McKay Creek | BOGONG1 | VIC | NVIC | Hydro | Hydro | Hydro | 1980 | 0 | 1 | 1 | N/A | 1 | 0 | 3600 | 3600 | 3600 | 3530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
McKay Creek | BOGONG2 | VIC | NVIC | Hydro | Hydro | Hydro | 1980 | 0 | 1 | 1 | N/A | 1 | 0 | 3600 | 3600 | 3600 | 3530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
McKay Creek | MCKAY11 | VIC | NVIC | Hydro | Hydro | Hydro | 1980 | 0 | 1 | 1 | N/A | 1 | 0 | 3600 | 3600 | 3600 | 3530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
McKay Creek | MCKAY12 | VIC | NVIC | Hydro | Hydro | Hydro | 1980 | 0 | 1 | 1 | N/A | 1 | 0 | 3600 | 3600 | 3600 | 3530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
McKay Creek | MCKAY13 | VIC | NVIC | Hydro | Hydro | Hydro | 1980 | 0 | 1 | 1 | N/A | 1 | 0 | 3600 | 3600 | 3600 | 3530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
McKay Creek | MCKAY14 | VIC | NVIC | Hydro | Hydro | Hydro | 1980 | 0 | 1 | 1 | N/A | 1 | 0 | 3600 | 3600 | 3600 | 3530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
McKay Creek | MCKAY15 | VIC | NVIC | Hydro | Hydro | Hydro | 1980 | 0 | 1 | 1 | N/A | 1 | 0 | 3600 | 3600 | 3600 | 3530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
McKay Creek | MCKAY16 | VIC | NVIC | Hydro | Hydro | Hydro | 1980 | 0 | 1 | 1 | N/A | 1 | 0 | 3600 | 3600 | 3600 | 3530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY01 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY02 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY03 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY04 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY05 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY06 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY07 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY08 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY09 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 1 | MURRAY10 | VIC | NVIC | Hydro | Hydro | Hydro | 1967 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 2 | MURRAY11 | VIC | NVIC | Hydro | Hydro | Hydro | 1969 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 2 | MURRAY12 | VIC | NVIC | Hydro | Hydro | Hydro | 1969 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 2 | MURRAY13 | VIC | NVIC | Hydro | Hydro | Hydro | 1969 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Murray 2 | MURRAY14 | VIC | NVIC | Hydro | Hydro | Hydro | 1969 | 0 | 1 | 1 | N/A | 1 | 0 | 11440 | 12000 | 2990 | 2530 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
West Kiewa | KWAGG1 | VIC | NVIC | Hydro | Hydro | Hydro | 1956 | 0 | 1 | 1 | N/A | 1 | 0 | 600 | 600 | 600 | 600 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
West Kiewa | KWAGG2 | VIC | NVIC | Hydro | Hydro | Hydro | 1956 | 0 | 1 | 1 | N/A | 1 | 0 | 600 | 600 | 600 | 600 | 100 |  |  | 7 | 56700 | 7 | 500 | 200 | 12 | 2 | 1 | 5 | 3 | 2 | 15000 | 3.52 | 2.02 | 30 | 4.126 | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 0 | 0
Kogan Creek | Kogan Creek Solar Boost | QLD | SWQ | ISCS | Solar | Kogan Creek | 2015 | 10 | 1 | 1 | N/A | 8 | 5 | 10000 | 10000 | 10000 | 10000 | 100 |  |  | 10 | 64000 | 15.2 | 500 | 200 | 5 | 3 | 1 | 5 | 3 | 2 | 25000 | 3 | 10 | 30 | 6 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 0 | 0
Hunter Valley | HVGTS1 | NSW | NCEN | OCGT | Distillate | Liquid Fuel | 1988 | 0 | 1 | 1 | 30 | 1 | 12 | 60 | 60 | 60 | 60 | 28 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 69.7 | 5.3
Hunter Valley | HVGTS2 | NSW | NCEN | OCGT | Distillate | Liquid Fuel | 1988 | 0 | 1 | 1 | 30 | 1 | 12 | 60 | 60 | 60 | 60 | 28 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 69.7 | 5.3
Mackay | MACKAYGT | QLD | NQ | OCGT | Distillate | Liquid Fuel | 1975 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 28 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 69.7 | 5.3
Mt Stuart | MSTUART1 | QLD | NQ | OCGT | Distillate | Liquid Fuel | 1998 | 0 | 1 | 1 | 30 | 1 | 4.6045 | 600 | 600 | 590 | 600 | 30 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 80.4606 | 5.3
Mt Stuart | MSTUART2 | QLD | NQ | OCGT | Distillate | Liquid Fuel | 1998 | 0 | 1 | 1 | 30 | 1 | 4.6045 | 600 | 600 | 590 | 600 | 30 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 80.4606 | 5.3
Mt Stuart | MSTUART3 | QLD | NQ | OCGT | Distillate | Liquid Fuel | 1998 | 0 | 1 | 1 | 30 | 1 | 4.6045 | 600 | 600 | 590 | 600 | 30 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 80.4606 | 5.3
Port Lincoln | POR01-1 | SA | NSA | OCGT | Distillate | Liquid Fuel | 1999 | 0 | 1 | 1 | 30 | 8 | 16 | 180 | 180 | 180 | 180 | 26 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 67.9 | 5.3
Port Lincoln | POR01-2 | SA | NSA | OCGT | Distillate | Liquid Fuel | 1999 | 0 | 1 | 1 | 30 | 8 | 16 | 180 | 180 | 180 | 180 | 26 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 67.9 | 5.3
Port Lincoln | POR01-3 | SA | NSA | OCGT | Distillate | Liquid Fuel | 1999 | 0 | 1 | 1 | 30 | 8 | 16 | 180 | 180 | 180 | 180 | 26 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 67.9 | 5.3
Snuggery | SNUG1 | SA | SESA | OCGT | Distillate | Liquid Fuel | 1997 | 0 | 1 | 1 | 30 | 3 | 14.2857 | 180 | 180 | 180 | 180 | 26 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 67.9 | 5.3
Snuggery | SNUG2 | SA | SESA | OCGT | Distillate | Liquid Fuel | 1997 | 0 | 1 | 1 | 30 | 3 | 14.2857 | 180 | 180 | 180 | 180 | 26 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 67.9 | 5.3
Snuggery | SNUG3 | SA | SESA | OCGT | Distillate | Liquid Fuel | 1997 | 0 | 1 | 1 | 30 | 3 | 14.2857 | 180 | 180 | 180 | 180 | 26 |  |  | 5 | 14200 | 10.4 | 600 | 500 | 6 | 1 | 1 | 100 | 100 | 100 | 6000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 67.9 | 5.3
Colongra GT | Colongra OCGT1 | NSW | NCEN | OCGT | Natural gas | Colongra | 2009 | 0 | 1 | 1 | 30 | 1 | 0 | 720 | 720 | 720 | 720 | 32 |  |  | 5 | 14200 | 8.3 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 58.9351 | 13.5
Colongra GT | Colongra OCGT2 | NSW | NCEN | OCGT | Natural gas | Colongra | 2009 | 0 | 1 | 1 | 30 | 1 | 0 | 720 | 720 | 720 | 720 | 32 |  |  | 5 | 14200 | 8.3 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 58.9351 | 13.5
Colongra GT | Colongra OCGT3 | NSW | NCEN | OCGT | Natural gas | Colongra | 2009 | 0 | 1 | 1 | 30 | 1 | 0 | 720 | 720 | 720 | 720 | 32 |  |  | 5 | 14200 | 8.3 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 58.9351 | 13.5
Colongra GT | Colongra OCGT4 | NSW | NCEN | OCGT | Natural gas | Colongra | 2009 | 0 | 1 | 1 | 30 | 1 | 0 | 720 | 720 | 720 | 720 | 32 |  |  | 5 | 14200 | 8.3 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 58.9351 | 13.5
Uranquinty | Uranquinty1 | NSW | SWNSW | OCGT | Natural gas | Uranquinty | 2009 | 0 | 1 | 1 | 30 | 1 | 1.2048 | 660 | 660 | 660 | 660 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 52.2289 | 13.5
Uranquinty | Uranquinty2 | NSW | SWNSW | OCGT | Natural gas | Uranquinty | 2009 | 0 | 1 | 1 | 30 | 1 | 1.2048 | 660 | 660 | 660 | 660 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 52.2289 | 13.5
Uranquinty | Uranquinty3 | NSW | SWNSW | OCGT | Natural gas | Uranquinty | 2009 | 0 | 1 | 1 | 30 | 1 | 1.2048 | 660 | 660 | 660 | 660 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 52.2289 | 13.5
Uranquinty | Uranquinty4 | NSW | SWNSW | OCGT | Natural gas | Uranquinty | 2009 | 0 | 1 | 1 | 30 | 1 | 1.2048 | 660 | 660 | 660 | 660 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 52.2289 | 13.5
Barcaldine | BARCALDN | QLD | CQ | OCGT | Natural gas | Barcaldine | 1996 | 0 | 4 | 4 | 30 | 1 | 8.1081 | 180 | 180 | 180 | 180 | 28 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 78.5634 | 7.6
Braemar | Braemar11 | QLD | SWQ | OCGT | Natural gas | Braemar | 2006 | 0 | 1 | 1 | 30 | 1 | 4.2683 | 430 | 460 | 430 | 460 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 48.0229 | 7.6
Braemar | Braemar12 | QLD | SWQ | OCGT | Natural gas | Braemar | 2006 | 0 | 1 | 1 | 30 | 1 | 4.2683 | 430 | 460 | 430 | 460 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 48.0229 | 7.6
Braemar | Braemar13 | QLD | SWQ | OCGT | Natural gas | Braemar | 2006 | 0 | 1 | 1 | 30 | 1 | 4.2683 | 430 | 460 | 430 | 460 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 48.0229 | 7.6
Braemar 2 | Braemar21 | QLD | SWQ | OCGT | Natural gas | Braemar 2 | 2009 | 0 | 1 | 1 | 30 | 1 | 4.6243 | 680 | 660 | 660 | 660 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 49.816 | 7.6
Braemar 2 | Braemar22 | QLD | SWQ | OCGT | Natural gas | Braemar 2 | 2009 | 0 | 1 | 1 | 30 | 1 | 4.6243 | 680 | 660 | 660 | 660 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 49.816 | 7.6
Braemar 2 | Braemar23 | QLD | SWQ | OCGT | Natural gas | Braemar 2 | 2009 | 0 | 1 | 1 | 30 | 1 | 4.6243 | 680 | 660 | 660 | 660 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 49.816 | 7.6
Oakey | OAKEY1 | QLD | SWQ | OCGT | Natural gas | Oakey | 2000 | 0 | 1 | 1 | 30 | 1 | 4.3318e-06 | 660 | 660 | 660 | 660 | 32.6 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 82.1174 | 7.6
Oakey | OAKEY2 | QLD | SWQ | OCGT | Natural gas | Oakey | 2000 | 0 | 1 | 1 | 30 | 1 | 4.3318e-06 | 660 | 660 | 660 | 660 | 32.6 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 82.1174 | 7.6
Roma | ROMA_7 | QLD | SWQ | OCGT | Natural gas | Roma | 1999 | 0 | 1 | 1 | 30 | 1 | 20.5882 | 480 | 480 | 480 | 480 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 55.8764 | 7.6
Roma | ROMA_8 | QLD | SWQ | OCGT | Natural gas | Roma | 1999 | 0 | 1 | 1 | 30 | 1 | 20.5882 | 480 | 480 | 480 | 480 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 55.8764 | 7.6
Dry Creek | DRYCGT1 | SA | ADE | OCGT | Natural gas | Dry Creek | 1973 | 0 | 1 | 1 | 30 | 1 | 18.3673 | 300 | 300 | 300 | 300 | 26 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 58.3614 | 10.2
Dry Creek | DRYCGT2 | SA | ADE | OCGT | Natural gas | Dry Creek | 1973 | 0 | 1 | 1 | 30 | 1 | 18.3673 | 300 | 300 | 300 | 300 | 26 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 58.3614 | 10.2
Dry Creek | DRYCGT3 | SA | ADE | OCGT | Natural gas | Dry Creek | 1973 | 0 | 1 | 1 | 30 | 1 | 18.3673 | 300 | 300 | 300 | 300 | 26 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 58.3614 | 10.2
Hallett | AGLHAL01 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL02 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL03 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL04 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL05 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL06 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL07 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL08 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL09 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL10 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL11 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Hallett | AGLHAL12 | SA | NSA | OCGT | Natural gas | Hallett | 2002 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 57.2391 | 10.2
Ladbroke Grove | LADBROK1 | SA | SESA | OCGT | Natural gas | Ladbroke Grove | 2000 | 0 | 1 | 1 | 30 | 1 | 12.5 | 480 | 480 | 480 | 480 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 46.3999 | 10.2
Ladbroke Grove | LADBROK2 | SA | SESA | OCGT | Natural gas | Ladbroke Grove | 2000 | 0 | 1 | 1 | 30 | 1 | 12.5 | 480 | 480 | 480 | 480 | 30 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 46.3999 | 10.2
Mintaro | MINTARO | SA | NSA | OCGT | Natural gas | Mintaro | 1984 | 0 | 1 | 1 | 30 | 1 | 17.7778 | 300 | 300 | 300 | 300 | 28 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 67.3788 | 10.2
Quarantine | QPS1 | SA | ADE | OCGT | Natural gas | Quarantine | 2002 | 0 | 1 | 1 | 30 | 5 | 8 | 600 | 600 | 600 | 600 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 64.4484 | 10.2
Quarantine | QPS2 | SA | ADE | OCGT | Natural gas | Quarantine | 2002 | 0 | 1 | 1 | 30 | 5 | 8 | 600 | 600 | 600 | 600 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 64.4484 | 10.2
Quarantine | QPS3 | SA | ADE | OCGT | Natural gas | Quarantine | 2002 | 0 | 1 | 1 | 30 | 5 | 8 | 600 | 600 | 600 | 600 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 64.4484 | 10.2
Quarantine | QPS4 | SA | ADE | OCGT | Natural gas | Quarantine | 2002 | 0 | 1 | 1 | 30 | 5 | 8 | 600 | 600 | 600 | 600 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 64.4484 | 10.2
Quarantine | QPS5 | SA | ADE | OCGT | Natural gas | Quarantine | 2002 | 0 | 1 | 1 | 30 | 5 | 8 | 600 | 600 | 600 | 600 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 64.4484 | 10.2
Bell Bay Three | Bell Bay GT1 | TAS | TAS | OCGT | Natural gas | Bell Bay Three | 2006 | 0 | 1 | 1 | 30 | 3 | 0 | 600 | 600 | 600 | 600 | 29 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 51.3 | 0
Bell Bay Three | Bell Bay GT2 | TAS | TAS | OCGT | Natural gas | Bell Bay Three | 2006 | 0 | 1 | 1 | 30 | 3 | 0 | 600 | 600 | 600 | 600 | 29 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 51.3 | 0
Bell Bay Three | Bell Bay GT3 | TAS | TAS | OCGT | Natural gas | Bell Bay Three | 2006 | 0 | 1 | 1 | 30 | 3 | 0 | 600 | 600 | 600 | 600 | 29 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 51.3 | 0
Tamar Valley OCGT | Tamar OCGT | TAS | TAS | OCGT | Natural gas | Tamar Valley OCGT | 2010 | 0 | 1 | 1 | 30 | 1 | 0 | 600 | 600 | 600 | 600 | 28 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 51.3 | 0
Bairnsdale | BDL01 | VIC | LV | OCGT | Natural gas | Bairnsdale | 2001 | 0 | 1 | 1 | 30 | 1 | 16.6667 | 240 | 240 | 240 | 240 | 34 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 50.0246 | 3.9
Bairnsdale | BDL02 | VIC | LV | OCGT | Natural gas | Bairnsdale | 2001 | 0 | 1 | 1 | 30 | 1 | 16.6667 | 240 | 240 | 240 | 240 | 34 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 50.0246 | 3.9
Jeeralang A | JLA01 | VIC | LV | OCGT | Natural gas | Jeeralang | 1979 | 0 | 1 | 1 | 30 | 3 | 9.434 | 540 | 540 | 540 | 540 | 22.9 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 53.7743 | 3.9
Jeeralang A | JLA02 | VIC | LV | OCGT | Natural gas | Jeeralang | 1979 | 0 | 1 | 1 | 30 | 3 | 9.434 | 540 | 540 | 540 | 540 | 22.9 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 53.7743 | 3.9
Jeeralang A | JLA03 | VIC | LV | OCGT | Natural gas | Jeeralang | 1979 | 0 | 1 | 1 | 30 | 3 | 9.434 | 540 | 540 | 540 | 540 | 22.9 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 53.7743 | 3.9
Jeeralang A | JLA04 | VIC | LV | OCGT | Natural gas | Jeeralang | 1979 | 0 | 1 | 1 | 30 | 3 | 9.434 | 540 | 540 | 540 | 540 | 22.9 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 53.7743 | 3.9
Jeeralang B | JLB01 | VIC | LV | OCGT | Natural gas | Jeeralang | 1980 | 0 | 1 | 1 | 30 | 3 | 5.2632 | 360 | 360 | 360 | 360 | 22.9 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 53.7743 | 3.9
Jeeralang B | JLB02 | VIC | LV | OCGT | Natural gas | Jeeralang | 1980 | 0 | 1 | 1 | 30 | 3 | 5.2632 | 360 | 360 | 360 | 360 | 22.9 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 53.7743 | 3.9
Jeeralang B | JLB03 | VIC | LV | OCGT | Natural gas | Jeeralang | 1980 | 0 | 1 | 1 | 30 | 3 | 5.2632 | 360 | 360 | 360 | 360 | 22.9 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 53.7743 | 3.9
Laverton North | Laverton North1 | VIC | MEL | OCGT | Natural gas | Laverton North | 2006 | 0 | 1 | 1 | 30 | 3 | 0 | 3330 | 3330 | 920 | 680 | 30.4 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 64.8916 | 3.9
Laverton North | Laverton North2 | VIC | MEL | OCGT | Natural gas | Laverton North | 2006 | 0 | 1 | 1 | 30 | 3 | 0 | 3330 | 3330 | 920 | 680 | 30.4 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 64.8916 | 3.9
Mortlake | Mortlake11 | VIC | MEL | OCGT | Natural gas | Mortlake OCGT | 2011 | 0 | 1 | 1 | 30 | 1 | 7.4733 | 780 | 780 | 780 | 780 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 46.1307 | 3.9
Mortlake | Mortlake12 | VIC | MEL | OCGT | Natural gas | Mortlake OCGT | 2011 | 0 | 1 | 1 | 30 | 1 | 7.4733 | 780 | 780 | 780 | 780 | 32 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 46.1307 | 3.9
Somerton | AGLSOM01 | VIC | MEL | OCGT | Natural gas | Somerton | 2002 | 0 | 1 | 1 | 30 | 1 | 17.1875 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 49.0557 | 3.9
Somerton | AGLSOM02 | VIC | MEL | OCGT | Natural gas | Somerton | 2002 | 0 | 1 | 1 | 30 | 1 | 17.1875 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 49.0557 | 3.9
Somerton | AGLSOM03 | VIC | MEL | OCGT | Natural gas | Somerton | 2002 | 0 | 1 | 1 | 30 | 1 | 17.1875 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 49.0557 | 3.9
Somerton | AGLSOM04 | VIC | MEL | OCGT | Natural gas | Somerton | 2002 | 0 | 1 | 1 | 30 | 1 | 17.1875 | 600 | 600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 49.0557 | 3.9
Valley Power | VPGS1 | VIC | LV | OCGT | Natural gas | Valley Power | 2002 | 0 | 1 | 1 | 30 | 1 | 10 | 3360 | 3600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 54.7886 | 3.9
Valley Power | VPGS2 | VIC | LV | OCGT | Natural gas | Valley Power | 2002 | 0 | 1 | 1 | 30 | 1 | 10 | 3360 | 3600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 54.7886 | 3.9
Valley Power | VPGS3 | VIC | LV | OCGT | Natural gas | Valley Power | 2002 | 0 | 1 | 1 | 30 | 1 | 10 | 3360 | 3600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 54.7886 | 3.9
Valley Power | VPGS4 | VIC | LV | OCGT | Natural gas | Valley Power | 2002 | 0 | 1 | 1 | 30 | 1 | 10 | 3360 | 3600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 54.7886 | 3.9
Valley Power | VPGS5 | VIC | LV | OCGT | Natural gas | Valley Power | 2002 | 0 | 1 | 1 | 30 | 1 | 10 | 3360 | 3600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 54.7886 | 3.9
Valley Power | VPGS6 | VIC | LV | OCGT | Natural gas | Valley Power | 2002 | 0 | 1 | 1 | 30 | 1 | 10 | 3360 | 3600 | 600 | 600 | 24 |  |  | 5 | 14200 | 10.4 | 500 | 200 | 6 | 1 | 1 | 100 | 100 | 100 | 5000 | 2 | 1 | 40 | 2.4 | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 54.7886 | 3.9
Bayswater | BW01 | NSW | NCEN | Steam turbine | Black Coal | Macquarie Generation | 1983 | 44.1176 | 8 | 8 | 10 | 6 | 0 | 120 | 310 | 100 | 230 | 35.9 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 91.8163 | 9.2
Bayswater | BW02 | NSW | NCEN | Steam turbine | Black Coal | Macquarie Generation | 1983 | 44.1176 | 8 | 8 | 10 | 6 | 0 | 120 | 310 | 100 | 230 | 35.9 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 91.8163 | 9.2
Bayswater | BW03 | NSW | NCEN | Steam turbine | Black Coal | Macquarie Generation | 1983 | 44.1176 | 8 | 8 | 10 | 6 | 0 | 120 | 310 | 100 | 230 | 35.9 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 91.8163 | 9.2
Bayswater | BW04 | NSW | NCEN | Steam turbine | Black Coal | Macquarie Generation | 1983 | 44.1176 | 8 | 8 | 10 | 6 | 0 | 120 | 310 | 100 | 230 | 35.9 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 91.8163 | 9.2
Eraring | ER01 | NSW | NCEN | Steam turbine | Black Coal | Eraring Energy | 1983 | 32 | 8 | 8 | 10 | 6 | 0 | 150 | 300 | 210 | 300 | 35.4 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.2088 | 9.2
Eraring | ER02 | NSW | NCEN | Steam turbine | Black Coal | Eraring Energy | 1983 | 32 | 8 | 8 | 10 | 6 | 0 | 150 | 300 | 210 | 300 | 35.4 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.2088 | 9.2
Eraring | ER03 | NSW | NCEN | Steam turbine | Black Coal | Eraring Energy | 1983 | 32 | 8 | 8 | 10 | 6 | 0 | 150 | 300 | 210 | 300 | 35.4 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.2088 | 9.2
Eraring | ER04 | NSW | NCEN | Steam turbine | Black Coal | Eraring Energy | 1983 | 32 | 8 | 8 | 10 | 6 | 0 | 150 | 300 | 210 | 300 | 35.4 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.2088 | 9.2
Liddell | LD01 | NSW | NCEN | Steam turbine | Black Coal | Macquarie Generation | 1972 | 43.8095 | 8 | 8 | 10 | 5 | 0 | 120 | 240 | 100 | 180 | 33.8 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.9054 | 9.2
Liddell | LD02 | NSW | NCEN | Steam turbine | Black Coal | Macquarie Generation | 1972 | 43.8095 | 8 | 8 | 10 | 5 | 0 | 120 | 240 | 100 | 180 | 33.8 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.9054 | 9.2
Liddell | LD03 | NSW | NCEN | Steam turbine | Black Coal | Macquarie Generation | 1972 | 43.8095 | 8 | 8 | 10 | 5 | 0 | 120 | 240 | 100 | 180 | 33.8 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.9054 | 9.2
Liddell | LD04 | NSW | NCEN | Steam turbine | Black Coal | Macquarie Generation | 1972 | 43.8095 | 8 | 8 | 10 | 5 | 0 | 120 | 240 | 100 | 180 | 33.8 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.9054 | 9.2
Mt Piper | MP1 | NSW | NCEN | Steam turbine | Black Coal | Delta Western | 1993 | 42 | 8 | 8 | 10 | 5 | 0 | 140 | 310 | 210 | 310 | 37 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 93.2854 | 9.2
Mt Piper | MP2 | NSW | NCEN | Steam turbine | Black Coal | Delta Western | 1993 | 42 | 8 | 8 | 10 | 5 | 0 | 140 | 310 | 210 | 310 | 37 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 93.2854 | 9.2
Redbank | REDBANK1 | NSW | NCEN | Steam turbine | Black Coal | Redbank | 2001 | 50 | 8 | 8 | 10 | 8 | 0 | 180 | 180 | 180 | 180 | 29.3 |  |  | 20 | 54000 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 105.0319 | 9.2
Vales Point B | VP5 | NSW | NCEN | Steam turbine | Black Coal | Delta Coastal | 1978 | 38 | 8 | 8 | 10 | 5 | 0 | 130 | 290 | 210 | 220 | 35.4 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 87.2535 | 9.2
Vales Point B | VP6 | NSW | NCEN | Steam turbine | Black Coal | Delta Coastal | 1978 | 38 | 8 | 8 | 10 | 5 | 0 | 130 | 290 | 210 | 220 | 35.4 |  |  | 20 | 53400 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 87.2535 | 9.2
Wallerawang C | WW7 | NSW | NCEN | Steam turbine | Black Coal | Delta Western | 1978 | 52.0833 | 8 | 8 | 10 | 7 | 0 | 80 | 180 | 150 | 180 | 33.1 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 85.507 | 9.2
Wallerawang C | WW8 | NSW | NCEN | Steam turbine | Black Coal | Delta Western | 1978 | 52.0833 | 8 | 8 | 10 | 7 | 0 | 80 | 180 | 150 | 180 | 33.1 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 85.507 | 9.2
Callide B | CALL_B_1 | QLD | CQ | Steam turbine | Black Coal | Callide B & C | 1989 | 49 | 8 | 8 | 10 | 9 | 0 | 180 | 190 | 180 | 190 | 36.1 |  |  | 20 | 54000 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 94.1942 | 2.3
Callide B | CALL_B_2 | QLD | CQ | Steam turbine | Black Coal | Callide B & C | 1989 | 49 | 8 | 8 | 10 | 9 | 0 | 180 | 190 | 180 | 190 | 36.1 |  |  | 20 | 54000 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 94.1942 | 2.3
Callide Power Plant | CPP_3 | QLD | CQ | Steam turbine | Black Coal | Callide B & C | 2001 | 49.3827 | 8 | 8 | 10 | 6 | 0 | 210 | 230 | 220 | 230 | 36.5 |  |  | 20 | 54000 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 96.5721 | 2.3
Callide Power Plant | CPP_4 | QLD | CQ | Steam turbine | Black Coal | Callide B & C | 2001 | 49.3827 | 8 | 8 | 10 | 6 | 0 | 210 | 230 | 220 | 230 | 36.5 |  |  | 20 | 54000 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 96.5721 | 2.3
Gladstone | GSTONE1 | QLD | CQ | Steam turbine | Black Coal | Gladstone | 1980 | 39.2857 | 8 | 8 | 10 | 8 | 0 | 180 | 290 | 190 | 300 | 35.2 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.3543 | 2.3
Gladstone | GSTONE2 | QLD | CQ | Steam turbine | Black Coal | Gladstone | 1980 | 39.2857 | 8 | 8 | 10 | 8 | 0 | 180 | 290 | 190 | 300 | 35.2 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.3543 | 2.3
Gladstone | GSTONE3 | QLD | CQ | Steam turbine | Black Coal | Gladstone | 1980 | 39.2857 | 8 | 8 | 10 | 8 | 0 | 180 | 290 | 190 | 300 | 35.2 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.3543 | 2.3
Gladstone | GSTONE4 | QLD | CQ | Steam turbine | Black Coal | Gladstone | 1980 | 39.2857 | 8 | 8 | 10 | 8 | 0 | 180 | 290 | 190 | 300 | 35.2 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.3543 | 2.3
Gladstone | GSTONE5 | QLD | CQ | Steam turbine | Black Coal | Gladstone | 1980 | 39.2857 | 8 | 8 | 10 | 8 | 0 | 180 | 290 | 190 | 300 | 35.2 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.3543 | 2.3
Gladstone | GSTONE6 | QLD | CQ | Steam turbine | Black Coal | Gladstone | 1980 | 39.2857 | 8 | 8 | 10 | 8 | 0 | 180 | 290 | 190 | 300 | 35.2 |  |  | 20 | 56700 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.3543 | 2.3
Kogan Creek | Kogan | QLD | SWQ | Steam turbine | Black Coal | Kogan Creek | 2007 | 46.6667 | 8 | 8 | 10 | 9 | 0 | 240 | 210 | 300 | 210 | 37.5 |  |  | 20 | 52300 | 0.5 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 87.0281 | 2.3
Millmerran | MPP_1 | QLD | SWQ | Steam turbine | Black Coal | Millmerran | 2002 | 40 | 8 | 8 | 10 | 6 | 10.7981 | 60 | 60 | 60 | 60 | 36.9 |  |  | 20 | 52300 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.5173 | 2.3
Millmerran | MPP_2 | QLD | SWQ | Steam turbine | Black Coal | Millmerran | 2002 | 40 | 8 | 8 | 10 | 6 | 10.7981 | 60 | 60 | 60 | 60 | 36.9 |  |  | 20 | 52300 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 90.5173 | 2.3
Stanwell | STAN-1 | QLD | CQ | Steam turbine | Black Coal | Stanwell | 1995 | 50 | 8 | 8 | 10 | 9 | 0 | 180 | 180 | 180 | 180 | 36.4 |  |  | 20 | 53400 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 95.6568 | 2.3
Stanwell | STAN-2 | QLD | CQ | Steam turbine | Black Coal | Stanwell | 1995 | 50 | 8 | 8 | 10 | 9 | 0 | 180 | 180 | 180 | 180 | 36.4 |  |  | 20 | 53400 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 95.6568 | 2.3
Stanwell | STAN-3 | QLD | CQ | Steam turbine | Black Coal | Stanwell | 1995 | 50 | 8 | 8 | 10 | 9 | 0 | 180 | 180 | 180 | 180 | 36.4 |  |  | 20 | 53400 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 95.6568 | 2.3
Stanwell | STAN-4 | QLD | CQ | Steam turbine | Black Coal | Stanwell | 1995 | 50 | 8 | 8 | 10 | 9 | 0 | 180 | 180 | 180 | 180 | 36.4 |  |  | 20 | 53400 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 95.6568 | 2.3
Tarong | TARONG1 | QLD | SWQ | Steam turbine | Black Coal | Tarong | 1985 | 40 | 8 | 8 | 10 | 8 | 0 | 200 | 240 | 200 | 240 | 36.2 |  |  | 20 | 54000 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 93.9976 | 2.3
Tarong | TARONG2 | QLD | SWQ | Steam turbine | Black Coal | Tarong | 1985 | 40 | 8 | 8 | 10 | 8 | 0 | 200 | 240 | 200 | 240 | 36.2 |  |  | 20 | 54000 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 93.9976 | 2.3
Tarong | TARONG3 | QLD | SWQ | Steam turbine | Black Coal | Tarong | 1985 | 40 | 8 | 8 | 10 | 8 | 0 | 200 | 240 | 200 | 240 | 36.2 |  |  | 20 | 54000 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 93.9976 | 2.3
Tarong | TARONG4 | QLD | SWQ | Steam turbine | Black Coal | Tarong | 1985 | 40 | 8 | 8 | 10 | 8 | 0 | 200 | 240 | 200 | 240 | 36.2 |  |  | 20 | 54000 | 3.1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 93.9976 | 2.3
Tarong North | TNPS1 | QLD | SWQ | Steam turbine | Black Coal | Tarong | 2002 | 39.5034 | 8 | 8 | 10 | 6 | 0 | 270 | 320 | 270 | 320 | 39.2 |  |  | 20 | 52300 | 1 | 1500 | 500 | 24 | 4 | 2 | 350 | 120 | 40 | 50000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 96.4941 | 2.3
Northern | NPS1 | SA | NSA | Steam turbine | Black Coal | Northern | 1985 | 56 | 16 | 16 | 10 | 10 | 0 | 180 | 180 | 180 | 180 | 34.9 |  |  | 20 | 60000 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 108.8088 | 0.8
Northern | NPS2 | SA | NSA | Steam turbine | Black Coal | Northern | 1985 | 56 | 16 | 16 | 10 | 10 | 0 | 180 | 180 | 180 | 180 | 34.9 |  |  | 20 | 60000 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 2.5 | 6 | 30 | 4.3 | 200 | 1500 | 20 | 8000 | 50 | 4000 | 108.8088 | 0.8
Anglesea | APS | VIC | CVIC | Steam turbine | Brown Coal | Anglesea | 1969 | 50 | 16 | 16 | 10 | 8 | 0 | 180 | 180 | 40 | 180 | 27.2 |  |  | 20 | 100000 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 92.4295 | 0.4
Energy Brix Complex | MOR1 | VIC | LV | Steam turbine | Brown Coal | Energy Brix | 1960 | 50 | 16 | 16 | 10 | 15 | 0 | 300 | 300 | 300 | 300 | 24 |  |  | 20 | 109000 | 2.1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 109.5145 | 0.4
Energy Brix Complex | MOR2 | VIC | LV | Steam turbine | Brown Coal | Energy Brix | 1960 | 50 | 16 | 16 | 10 | 15 | 0 | 300 | 300 | 300 | 300 | 24 |  |  | 20 | 109000 | 2.1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 109.5145 | 0.4
Energy Brix Complex | MOR3 | VIC | LV | Steam turbine | Brown Coal | Energy Brix | 1960 | 50 | 16 | 16 | 10 | 15 | 0 | 300 | 300 | 300 | 300 | 24 |  |  | 20 | 109000 | 2.1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 109.5145 | 0.4
Hazelwood | HWPS1 | VIC | LV | Steam turbine | Brown Coal | Hazelwood | 1968 | 63.4146 | 16 | 16 | 10 | 10 | 0 | 120 | 120 | 120 | 120 | 22 |  |  | 20 | 152600 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 94.8112 | 0.4
Hazelwood | HWPS2 | VIC | LV | Steam turbine | Brown Coal | Hazelwood | 1968 | 63.4146 | 16 | 16 | 10 | 10 | 0 | 120 | 120 | 120 | 120 | 22 |  |  | 20 | 152600 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 94.8112 | 0.4
Hazelwood | HWPS3 | VIC | LV | Steam turbine | Brown Coal | Hazelwood | 1968 | 63.4146 | 16 | 16 | 10 | 10 | 0 | 120 | 120 | 120 | 120 | 22 |  |  | 20 | 152600 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 94.8112 | 0.4
Hazelwood | HWPS4 | VIC | LV | Steam turbine | Brown Coal | Hazelwood | 1968 | 63.4146 | 16 | 16 | 10 | 10 | 0 | 120 | 120 | 120 | 120 | 22 |  |  | 20 | 152600 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 94.8112 | 0.4
Hazelwood | HWPS5 | VIC | LV | Steam turbine | Brown Coal | Hazelwood | 1968 | 63.4146 | 16 | 16 | 10 | 10 | 0 | 120 | 120 | 120 | 120 | 22 |  |  | 20 | 152600 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 94.8112 | 0.4
Hazelwood | HWPS6 | VIC | LV | Steam turbine | Brown Coal | Hazelwood | 1968 | 63.4146 | 16 | 16 | 10 | 10 | 0 | 120 | 120 | 120 | 120 | 22 |  |  | 20 | 152600 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 94.8112 | 0.4
Hazelwood | HWPS7 | VIC | LV | Steam turbine | Brown Coal | Hazelwood | 1968 | 63.4146 | 16 | 16 | 10 | 10 | 0 | 120 | 120 | 120 | 120 | 22 |  |  | 20 | 152600 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 94.8112 | 0.4
Hazelwood | HWPS8 | VIC | LV | Steam turbine | Brown Coal | Hazelwood | 1968 | 63.4146 | 16 | 16 | 10 | 10 | 0 | 120 | 120 | 120 | 120 | 22 |  |  | 20 | 152600 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 94.8112 | 0.4
Loy Yang A | LYA1 | VIC | LV | Steam turbine | Brown Coal | Loy Yang A | 1986 | 62 | 16 | 16 | 10 | 9 | 0 | 350 | 330 | 430 | 320 | 27.2 |  |  | 20 | 141700 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 96.2955 | 0.4
Loy Yang A | LYA2 | VIC | LV | Steam turbine | Brown Coal | Loy Yang A | 1986 | 62 | 16 | 16 | 10 | 9 | 0 | 350 | 330 | 430 | 320 | 27.2 |  |  | 20 | 141700 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 96.2955 | 0.4
Loy Yang A | LYA3 | VIC | LV | Steam turbine | Brown Coal | Loy Yang A | 1986 | 62 | 16 | 16 | 10 | 9 | 0 | 350 | 330 | 430 | 320 | 27.2 |  |  | 20 | 141700 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 96.2955 | 0.4
Loy Yang A | LYA4 | VIC | LV | Steam turbine | Brown Coal | Loy Yang A | 1986 | 62 | 16 | 16 | 10 | 9 | 0 | 350 | 330 | 430 | 320 | 27.2 |  |  | 20 | 141700 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 96.2955 | 0.4
Loy Yang B | LOYYB1 | VIC | LV | Steam turbine | Brown Coal | Loy Yang B | 1995 | 60.9524 | 16 | 16 | 10 | 8 | 3.5 | 450 | 540 | 450 | 540 | 26.6 |  |  | 20 | 112000 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 91.2445 | 0.4
Loy Yang B | LOYYB2 | VIC | LV | Steam turbine | Brown Coal | Loy Yang B | 1995 | 60.9524 | 16 | 16 | 10 | 8 | 3.5 | 450 | 540 | 450 | 540 | 26.6 |  |  | 20 | 112000 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 91.2445 | 0.4
Yallourn | YWPS1 | VIC | LV | Steam turbine | Brown Coal | Yallourn | 1980 | 60 | 16 | 16 | 10 | 10 | 2.7778 | 130 | 260 | 140 | 260 | 23.5 |  |  | 20 | 147200 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 96.955 | 0.4
Yallourn | YWPS2 | VIC | LV | Steam turbine | Brown Coal | Yallourn | 1980 | 60 | 16 | 16 | 10 | 10 | 2.7778 | 130 | 260 | 140 | 260 | 23.5 |  |  | 20 | 147200 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 96.955 | 0.4
Yallourn | YWPS3 | VIC | LV | Steam turbine | Brown Coal | Yallourn | 1980 | 60 | 16 | 16 | 10 | 10 | 2.7778 | 130 | 260 | 140 | 260 | 23.5 |  |  | 20 | 147200 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 96.955 | 0.4
Yallourn | YWPS4 | VIC | LV | Steam turbine | Brown Coal | Yallourn | 1980 | 60 | 16 | 16 | 10 | 10 | 2.7778 | 130 | 260 | 140 | 260 | 23.5 |  |  | 20 | 147200 | 1 | 1500 | 500 | 48 | 4 | 2 | 350 | 120 | 40 | 80000 | 3 | 10 | 30 | 6 | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 96.955 | 0.4
Torrens Island A | TORRA1 | SA | ADE | Steam turbine | Natural gas | Torrens Island | 1967 | 0 | 1 | 1 | 30 | 5 | 0 | 220 | 290 | 40 | 300 | 30 |  |  | 2.5 | 42500 | 2.1 | 1200 | 400 | 20 | 4 | 2 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 50.0351 | 10.2
Torrens Island A | TORRA2 | SA | ADE | Steam turbine | Natural gas | Torrens Island | 1967 | 0 | 1 | 1 | 30 | 5 | 0 | 220 | 290 | 40 | 300 | 30 |  |  | 2.5 | 42500 | 2.1 | 1200 | 400 | 20 | 4 | 2 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 50.0351 | 10.2
Torrens Island A | TORRA3 | SA | ADE | Steam turbine | Natural gas | Torrens Island | 1967 | 0 | 1 | 1 | 30 | 5 | 0 | 220 | 290 | 40 | 300 | 30 |  |  | 2.5 | 42500 | 2.1 | 1200 | 400 | 20 | 4 | 2 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 50.0351 | 10.2
Torrens Island A | TORRA4 | SA | ADE | Steam turbine | Natural gas | Torrens Island | 1967 | 0 | 1 | 1 | 30 | 5 | 0 | 220 | 290 | 40 | 300 | 30 |  |  | 2.5 | 42500 | 2.1 | 1200 | 400 | 20 | 4 | 2 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 50.0351 | 10.2
Torrens Island B | TORRB1 | SA | ADE | Steam turbine | Natural gas | Torrens Island | 1977 | 0 | 1 | 1 | 30 | 5 | 0 | 410 | 450 | 280 | 300 | 32 |  |  | 2.5 | 42500 | 2.1 | 1200 | 400 | 20 | 4 | 2 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 49.1228 | 10.2
Torrens Island B | TORRB2 | SA | ADE | Steam turbine | Natural gas | Torrens Island | 1977 | 0 | 1 | 1 | 30 | 5 | 0 | 410 | 450 | 280 | 300 | 32 |  |  | 2.5 | 42500 | 2.1 | 1200 | 400 | 20 | 4 | 2 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 49.1228 | 10.2
Torrens Island B | TORRB3 | SA | ADE | Steam turbine | Natural gas | Torrens Island | 1977 | 0 | 1 | 1 | 30 | 5 | 0 | 410 | 450 | 280 | 300 | 32 |  |  | 2.5 | 42500 | 2.1 | 1200 | 400 | 20 | 4 | 2 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 49.1228 | 10.2
Torrens Island B | TORRB4 | SA | ADE | Steam turbine | Natural gas | Torrens Island | 1977 | 0 | 1 | 1 | 30 | 5 | 0 | 410 | 450 | 280 | 300 | 32 |  |  | 2.5 | 42500 | 2.1 | 1200 | 400 | 20 | 4 | 2 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 49.1228 | 10.2
Newport | NPS | VIC | MEL | Steam turbine | Natural gas | Newport | 1980 | 0 | 1 | 1 | 30 | 5 | 6.8627 | 340 | 420 | 340 | 420 | 33.3 |  |  | 2.5 | 43600 | 12.5 | 500 | 200 | 12 | 3 | 1 | 20 | 10 | 5 | 5000 | 1.44 | 3.3 | 17.71 | 2.0244 | 5304.02 | 991.05 | 190.21 | 5579.88 | 14.87 | 10838151735 | 50.851 | 3.9
Boco Rock Wind Farm | Boco Rock Wind Farm | NSW | CAN | Wind | Wind | Wind | 2015 | 0 | 1 | 1 | 0 | 1 | 0 | 620 | 630 | 600 | 620 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 12 | 2 | 1 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Gullen Range | Gullen Range | NSW | CAN | Wind | Wind | Wind | 2014 | 0 | 1 | 1 | 0 | 1 | 0 | 5000 | 5000 | 5000 | 5000 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Gunning | Gunning | NSW | CAN | Wind | Wind | Wind | 2011 | 0 | 1 | 1 | 0 | 1 | 0 | 2820 | 2820 | 2820 | 2820 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Taralga Wind Farm | Taralga | NSW | NCEN | Wind | Wind | Wind | 2014 | 0 | 1 | 1 | 0 | 1 | 0 | 620 | 630 | 600 | 620 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Woodlawn Wind Farm | Woodlawn | NSW | CAN | Wind | Wind | Wind | 2011 | 0 | 1 | 1 | 0 | 1 | 0 | 900 | 900 | 180 | 180 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Clements Gap Wind Farm | Clements Gap | SA | NSA | Wind | Wind | Wind | 2010 | 0 | 1 | 1 | 0 | 1 | 0 | 1790 | 1790 | 1790 | 1790 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Hallett 1 Wind Farm | Hallett Wind Farm | SA | NSA | Wind | Wind | Wind | 2007 | 0 | 1 | 1 | 0 | 1 | 0 | 180 | 180 | 180 | 180 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Hallett 2 Wind Farm | Hallett Hill Wind Farm | SA | NSA | Wind | Wind | Wind | 2009 | 0 | 1 | 1 | 0 | 1 | 0 | 120 | 120 | 120 | 120 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Hallett 4 Wind Farm | North Brown Hill | SA | NSA | Wind | Wind | Wind | 2011 | 0 | 1 | 1 | 0 | 1 | 0 | 180 | 180 | 180 | 180 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Hallett 5 Wind Farm | Hallett 5 The Bluff | SA | NSA | Wind | Wind | Wind | 2012 | 0 | 1 | 1 | 0 | 1 | 0 | 120 | 120 | 120 | 120 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Lake Bonney 2 Wind Farm | LKBONNY2 | SA | SESA | Wind | Wind | Wind | 2008 | 0 | 1 | 1 | 0 | 1 | 0 | 780 | 780 | 780 | 780 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Lake Bonney 3 Wind Farm | LKBONNY3 | SA | SESA | Wind | Wind | Wind | 2011 | 0 | 1 | 1 | 0 | 1 | 0 | 900 | 900 | 180 | 180 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Snowtown 2 North | Snowtown 2 North | SA | ADE | Wind | Wind | Wind | 2014 | 0 | 1 | 1 | 0 | 1 | 0 | 620 | 630 | 600 | 620 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Snowtown 2 South | Snowtown 2 South | SA | ADE | Wind | Wind | Wind | 2014 | 0 | 1 | 1 | 0 | 1 | 0 | 620 | 630 | 600 | 620 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Snowtown Wind Farm | Snowtown Wind Farm | SA | NSA | Wind | Wind | Wind | 2008 | 0 | 1 | 1 | 0 | 1 | 0 | 600 | 600 | 600 | 600 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Waterloo | Waterloo | SA | NSA | Wind | Wind | Wind | 2011 | 0 | 1 | 1 | 0 | 1 | 0 | 1510 | 1580 | 1510 | 1580 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Musselroe Wind Farm | Musselroe | TAS | TAS | Wind | Wind | Wind | 2012 | 0 | 1 | 1 | 0 | 1 | 0 | 9740 | 10080 | 9740 | 10080 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Macarthur | Macarthur | VIC | CVIC | Wind | Wind | Wind | 2012 | 0 | 1 | 1 | 0 | 1 | 0 | 480 | 560 | 470 | 560 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Mt Mercer | Mt Mercer | VIC | CVIC | Wind | Wind | Wind | 2014 | 0 | 1 | 1 | 0 | 1 | 0 | 620 | 630 | 600 | 620 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Oaklands Hill | Oaklands Hill | VIC | CVIC | Wind | Wind | Wind | 2011 | 0 | 1 | 1 | 0 | 1 | 0 | 620 | 630 | 600 | 620 | 100 |  |  | 3 | 43000 | 10 | 2000 | 1000 | 0 | 0 | 0 | 5 | 3 | 2 | 10000 | 5 | 20 | 15 | 8 | 500 | 10000 | 10000 | 12000 | 600 | 800 | 0 | 0
Note on O18: Richard Lenton: ACCIONA said ramp rates are not applicable - but they use them in their offer curves
Note on AK70: Richard Lenton: need to check - may include planned as well

## Existing Fuel Costs
Fuel Costs for Existing Units (2014-15 $/GJ)
Year Ending June
Profile | Scenario | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Anglesea | High | 0.42546 | 0.42972 | 0.43401 | 0.43835 | 0.44274 | 0.44717 | 0.45164 | 0.45615 | 0.46072 | 0.46532 | 0.46998 | 0.47468 | 0.47942 | 0.48422 | 0.48906 | 0.49395 | 0.49889 | 0.50388 | 0.50892 | 0.51401 | 0.51915 | 0.52434 | 0.52958 | 0.53488 | 0.54022 | 0.54563 | 0.5509 | 0.55622 | 0.56154 | 0.56686 | 0.57219
Callide B & C | High | 1.5 | 1.7827 | 1.7679 | 1.9927 | 2.0634 | 2.0529 | 2.0396 | 2.0191 | 1.9941 | 1.9702 | 1.9472 | 1.9254 | 1.9088 | 1.899 | 1.8894 | 1.8791 | 1.8692 | 1.8602 | 1.8525 | 1.8458 | 1.8402 | 1.8354 | 1.8313 | 1.8276 | 1.8243 | 1.8211 | 1.8173 | 1.8137 | 1.8102 | 1.8066 | 1.8031
Delta Coastal | High | 2.6863 | 2.5905 | 2.583 | 2.7708 | 2.8505 | 2.8318 | 2.8004 | 2.8121 | 3.4738 | 3.4344 | 3.3967 | 3.3608 | 3.3335 | 3.3173 | 3.3015 | 3.2847 | 3.2685 | 3.2537 | 3.2409 | 3.2299 | 3.2207 | 3.2129 | 3.206 | 3.2 | 3.1945 | 3.1894 | 3.183 | 3.1772 | 3.1713 | 3.1655 | 3.1596
Delta Western | High | 2.8991 | 2.6793 | 2.6549 | 3.0252 | 3.1416 | 3.1244 | 3.1024 | 3.0686 | 3.0275 | 2.9881 | 2.9502 | 2.9143 | 2.8869 | 2.8708 | 2.855 | 2.8381 | 2.8218 | 2.807 | 2.7942 | 2.7832 | 2.774 | 2.7661 | 2.7593 | 2.7533 | 2.7477 | 2.7426 | 2.7362 | 2.7304 | 2.7245 | 2.7186 | 2.7128
Energy Brix | High | 0.64314 | 0.64957 | 0.65607 | 0.66263 | 0.66926 | 0.67595 | 0.68271 | 0.68953 | 0.69643 | 0.70339 | 0.71043 | 0.71753 | 0.72471 | 0.73195 | 0.73927 | 0.74667 | 0.75413 | 0.76168 | 0.76929 | 0.77698 | 0.78475 | 0.7926 | 0.80053 | 0.80853 | 0.81662 | 0.82478 | 0.83275 | 0.8408 | 0.84884 | 0.85689 | 0.86493
Eraring Energy | High | 2.84 | 2.9252 | 2.6232 | 2.6294 | 2.6665 | 2.6678 | 2.6123 | 3.5149 | 3.4738 | 3.4344 | 3.3967 | 3.3608 | 3.3335 | 3.3173 | 3.3015 | 3.2847 | 3.2685 | 3.2537 | 3.2409 | 3.2299 | 3.2207 | 3.2129 | 3.206 | 3.2 | 3.1945 | 3.1894 | 3.183 | 3.1772 | 3.1713 | 3.1655 | 3.1596
Gladstone | High | 2.9067 | 2.7278 | 2.708 | 3.0094 | 3.1041 | 3.0901 | 3.0722 | 3.0447 | 3.0112 | 2.9791 | 2.9483 | 2.9191 | 2.8968 | 2.8836 | 2.8708 | 2.8571 | 2.8438 | 2.8317 | 2.8213 | 2.8124 | 2.8049 | 2.7985 | 2.7929 | 2.788 | 2.7835 | 2.7793 | 2.7741 | 2.7694 | 2.7646 | 2.7598 | 2.7551
Hazelwood | High | 0.08905 | 0.090831 | 0.092648 | 0.094501 | 0.096391 | 0.098319 | 0.10029 | 0.10229 | 0.10434 | 0.10642 | 0.10855 | 0.11072 | 0.11294 | 0.1152 | 0.1175 | 0.11985 | 0.12225 | 0.12469 | 0.12719 | 0.12973 | 0.13232 | 0.13497 | 0.13767 | 0.14042 | 0.14323 | 0.1461 | 0.14882 | 0.1516 | 0.15439 | 0.15717 | 0.15995
Kogan Creek | High | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904
Loy Yang A | High | 0.08905 | 0.090831 | 0.092648 | 0.094501 | 0.096391 | 0.098319 | 0.10029 | 0.10229 | 0.10434 | 0.10642 | 0.10855 | 0.11072 | 0.11294 | 0.1152 | 0.1175 | 0.11985 | 0.12225 | 0.12469 | 0.12719 | 0.12973 | 0.13232 | 0.13497 | 0.13767 | 0.14042 | 0.14323 | 0.1461 | 0.14882 | 0.1516 | 0.15439 | 0.15717 | 0.15995
Loy Yang B | High | 0.39578 | 0.39974 | 0.40373 | 0.40777 | 0.41185 | 0.41597 | 0.42013 | 0.42433 | 0.42857 | 0.43286 | 0.43719 | 0.44156 | 0.44597 | 0.45043 | 0.45494 | 0.45949 | 0.46408 | 0.46872 | 0.47341 | 0.47814 | 0.48293 | 0.48776 | 0.49263 | 0.49756 | 0.50253 | 0.50756 | 0.51246 | 0.51741 | 0.52236 | 0.52732 | 0.53227
Macquarie Generation | High | 1.6238 | 1.6516 | 1.7058 | 1.9004 | 2.0335 | 2.1017 | 2.1423 | 2.1424 | 2.1329 | 2.1196 | 2.141 | 2.2953 | 2.9135 | 2.899 | 2.8848 | 2.8697 | 2.8551 | 2.8419 | 2.8304 | 2.8206 | 2.8124 | 2.8054 | 2.7993 | 2.7939 | 2.789 | 2.7843 | 2.7787 | 2.7734 | 2.7682 | 2.763 | 2.7577
Millmerran | High | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957
Northern | High | 1.6425 | 1.6753 | 1.7088 | 1.743 | 2.2935 | 2.3393 | 2.3861 | 2.4338 | 2.4825 | 2.5322 | 2.5828 | 2.6345 | 2.6872 | 2.7409 | 2.7957 | 2.8516 | 2.9087 | 2.9668 | 3.0262 | 3.0867 | 3.1484 | 3.2114 | 3.2756 | 3.3411 | 3.408 | 3.4761 | 3.541 | 3.6072 | 3.6733 | 3.7395 | 3.8057
Redbank | High | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
Stanwell | High | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 2.639 | 2.626 | 2.6133 | 2.5997 | 2.5866 | 2.5747 | 2.5643 | 2.5555 | 2.5481 | 2.5417 | 2.5362 | 2.5314 | 2.5269 | 2.5228 | 2.5176 | 2.5129 | 2.5082 | 2.5035 | 2.4988
Tarong | High | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Yallourn | High | 0.098945 | 0.10092 | 0.10294 | 0.105 | 0.1071 | 0.10924 | 0.11143 | 0.11366 | 0.11593 | 0.11825 | 0.12061 | 0.12303 | 0.12549 | 0.128 | 0.13056 | 0.13317 | 0.13583 | 0.13855 | 0.14132 | 0.14414 | 0.14703 | 0.14997 | 0.15297 | 0.15603 | 0.15915 | 0.16233 | 0.16536 | 0.16845 | 0.17154 | 0.17463 | 0.17772
Anglesea | Low | 0.42546 | 0.42972 | 0.43401 | 0.43835 | 0.44274 | 0.44717 | 0.45164 | 0.45615 | 0.46072 | 0.46532 | 0.46998 | 0.47468 | 0.47942 | 0.48422 | 0.48906 | 0.49395 | 0.49889 | 0.50388 | 0.50892 | 0.51401 | 0.51915 | 0.52434 | 0.52958 | 0.53488 | 0.54022 | 0.54563 | 0.5509 | 0.55622 | 0.56154 | 0.56686 | 0.57219
Callide B & C | Low | 1.5 | 1.8956 | 1.7705 | 1.6358 | 1.6298 | 1.6258 | 1.6132 | 1.5954 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845 | 1.5845
Delta Coastal | Low | 2.7336 | 2.6756 | 2.5777 | 2.4747 | 2.478 | 2.4674 | 2.4442 | 2.4432 | 2.7856 | 2.7551 | 2.7253 | 2.6968 | 2.6752 | 2.6631 | 2.6514 | 2.6387 | 2.6262 | 2.6145 | 2.6042 | 2.595 | 2.5868 | 2.5793 | 2.5723 | 2.5656 | 2.5591 | 2.5528 | 2.5459 | 2.5393 | 2.5327 | 2.5261 | 2.5194
Delta Western | Low | 3.0021 | 2.8652 | 2.6592 | 2.4374 | 2.4275 | 2.4208 | 2.4 | 2.3707 | 2.3382 | 2.3076 | 2.2778 | 2.2492 | 2.2276 | 2.2154 | 2.2037 | 2.191 | 2.1784 | 2.1668 | 2.1565 | 2.1472 | 2.139 | 2.1315 | 2.1244 | 2.1178 | 2.1112 | 2.1049 | 2.0981 | 2.0914 | 2.0848 | 2.0782 | 2.0715
Energy Brix | Low | 0.64314 | 0.64957 | 0.65607 | 0.66263 | 0.66926 | 0.67595 | 0.68271 | 0.68953 | 0.69643 | 0.70339 | 0.71043 | 0.71753 | 0.72471 | 0.73195 | 0.73927 | 0.74667 | 0.75413 | 0.76168 | 0.76929 | 0.77698 | 0.78475 | 0.7926 | 0.80053 | 0.80853 | 0.81662 | 0.82478 | 0.83275 | 0.8408 | 0.84884 | 0.85689 | 0.86493
Eraring Energy | Low | 2.84 | 2.923 | 2.6073 | 2.5717 | 2.5643 | 2.5553 | 2.5273 | 2.8181 | 2.7856 | 2.7551 | 2.7253 | 2.6968 | 2.6752 | 2.6631 | 2.6514 | 2.6387 | 2.6262 | 2.6145 | 2.6042 | 2.595 | 2.5868 | 2.5793 | 2.5723 | 2.5656 | 2.5591 | 2.5528 | 2.5459 | 2.5393 | 2.5327 | 2.5261 | 2.5194
Gladstone | Low | 2.9905 | 2.8791 | 2.7114 | 2.5309 | 2.5228 | 2.5174 | 2.5005 | 2.4766 | 2.4546 | 2.439 | 2.4237 | 2.4092 | 2.3981 | 2.3919 | 2.3859 | 2.3794 | 2.373 | 2.3671 | 2.3618 | 2.3571 | 2.3529 | 2.3491 | 2.3455 | 2.3421 | 2.3387 | 2.3355 | 2.332 | 2.3286 | 2.3253 | 2.3219 | 2.3185
Hazelwood | Low | 0.08905 | 0.090831 | 0.092648 | 0.094501 | 0.096391 | 0.098319 | 0.10029 | 0.10229 | 0.10434 | 0.10642 | 0.10855 | 0.11072 | 0.11294 | 0.1152 | 0.1175 | 0.11985 | 0.12225 | 0.12469 | 0.12719 | 0.12973 | 0.13232 | 0.13497 | 0.13767 | 0.14042 | 0.14323 | 0.1461 | 0.14882 | 0.1516 | 0.15439 | 0.15717 | 0.15995
Kogan Creek | Low | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904
Loy Yang A | Low | 0.08905 | 0.090831 | 0.092648 | 0.094501 | 0.096391 | 0.098319 | 0.10029 | 0.10229 | 0.10434 | 0.10642 | 0.10855 | 0.11072 | 0.11294 | 0.1152 | 0.1175 | 0.11985 | 0.12225 | 0.12469 | 0.12719 | 0.12973 | 0.13232 | 0.13497 | 0.13767 | 0.14042 | 0.14323 | 0.1461 | 0.14882 | 0.1516 | 0.15439 | 0.15717 | 0.15995
Loy Yang B | Low | 0.39578 | 0.39974 | 0.40373 | 0.40777 | 0.41185 | 0.41597 | 0.42013 | 0.42433 | 0.42857 | 0.43286 | 0.43719 | 0.44156 | 0.44597 | 0.45043 | 0.45494 | 0.45949 | 0.46408 | 0.46872 | 0.47341 | 0.47814 | 0.48293 | 0.48776 | 0.49263 | 0.49756 | 0.50253 | 0.50756 | 0.51246 | 0.51741 | 0.52236 | 0.52732 | 0.53227
Macquarie Generation | Low | 1.6369 | 1.6789 | 1.6992 | 1.7437 | 1.8059 | 1.8521 | 1.8765 | 1.8747 | 1.8692 | 1.8606 | 1.8738 | 1.9703 | 2.3233 | 2.3125 | 2.302 | 2.2905 | 2.2793 | 2.2689 | 2.2597 | 2.2514 | 2.2441 | 2.2374 | 2.2311 | 2.2251 | 2.2193 | 2.2136 | 2.2075 | 2.2016 | 2.1957 | 2.1897 | 2.1838
Millmerran | Low | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957
Northern | Low | 1.6425 | 1.6753 | 1.7088 | 1.743 | 2.2935 | 2.3393 | 2.3861 | 2.4338 | 2.4825 | 2.5322 | 2.5828 | 2.6345 | 2.6872 | 2.7409 | 2.7957 | 2.8516 | 2.9087 | 2.9668 | 3.0262 | 3.0867 | 3.1484 | 3.2114 | 3.2756 | 3.3411 | 3.408 | 3.4761 | 3.541 | 3.6072 | 3.6733 | 3.7395 | 3.8057
Redbank | Low | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
Stanwell | Low | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 2.1079 | 2.0981 | 2.0887 | 2.0784 | 2.0683 | 2.0589 | 2.0506 | 2.0432 | 2.0365 | 2.0305 | 2.0248 | 2.0194 | 2.0142 | 2.0091 | 2.0036 | 1.9982 | 1.9929 | 1.9875 | 1.9822
Tarong | Low | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Yallourn | Low | 0.098945 | 0.10092 | 0.10294 | 0.105 | 0.1071 | 0.10924 | 0.11143 | 0.11366 | 0.11593 | 0.11825 | 0.12061 | 0.12303 | 0.12549 | 0.128 | 0.13056 | 0.13317 | 0.13583 | 0.13855 | 0.14132 | 0.14414 | 0.14703 | 0.14997 | 0.15297 | 0.15603 | 0.15915 | 0.16233 | 0.16536 | 0.16845 | 0.17154 | 0.17463 | 0.17772
Anglesea | Medium | 0.42546 | 0.42972 | 0.43401 | 0.43835 | 0.44274 | 0.44717 | 0.45164 | 0.45615 | 0.46072 | 0.46532 | 0.46998 | 0.47468 | 0.47942 | 0.48422 | 0.48906 | 0.49395 | 0.49889 | 0.50388 | 0.50892 | 0.51401 | 0.51915 | 0.52434 | 0.52958 | 0.53488 | 0.54022 | 0.54563 | 0.5509 | 0.55622 | 0.56154 | 0.56686 | 0.57219
Callide B & C | Medium | 1.5 | 1.843 | 1.782 | 1.8244 | 1.8511 | 1.8396 | 1.8258 | 1.8091 | 1.7889 | 1.7697 | 1.7504 | 1.7303 | 1.7125 | 1.7033 | 1.6959 | 1.6883 | 1.6806 | 1.6732 | 1.6662 | 1.6599 | 1.6543 | 1.6493 | 1.6448 | 1.6406 | 1.6367 | 1.6359 | 1.6309 | 1.6274 | 1.6239 | 1.6204 | 1.6169
Delta Coastal | Medium | 2.7085 | 2.6355 | 2.5892 | 2.6292 | 2.6656 | 2.6468 | 2.6181 | 2.6253 | 3.1369 | 3.1054 | 3.0739 | 3.0407 | 3.0111 | 2.9959 | 2.9839 | 2.9715 | 2.959 | 2.9468 | 2.9354 | 2.925 | 2.9158 | 2.9075 | 2.9001 | 2.8933 | 2.8867 | 2.8857 | 2.8775 | 2.8718 | 2.8661 | 2.8604 | 2.8547
Delta Western | Medium | 2.9473 | 2.778 | 2.6766 | 2.7464 | 2.7909 | 2.7728 | 2.7502 | 2.7224 | 2.6888 | 2.6569 | 2.625 | 2.5919 | 2.5631 | 2.5481 | 2.5358 | 2.523 | 2.5102 | 2.4978 | 2.4864 | 2.476 | 2.4668 | 2.4586 | 2.4512 | 2.4444 | 2.4378 | 2.4361 | 2.4281 | 2.4223 | 2.4164 | 2.4106 | 2.4047
Energy Brix | Medium | 0.64314 | 0.64957 | 0.65607 | 0.66263 | 0.66926 | 0.67595 | 0.68271 | 0.68953 | 0.69643 | 0.70339 | 0.71043 | 0.71753 | 0.72471 | 0.73195 | 0.73927 | 0.74667 | 0.75413 | 0.76168 | 0.76929 | 0.77698 | 0.78475 | 0.7926 | 0.80053 | 0.80853 | 0.81662 | 0.82478 | 0.83275 | 0.8408 | 0.84884 | 0.85689 | 0.86493
Eraring Energy | Medium | 2.84 | 2.9222 | 2.6128 | 2.5965 | 2.6103 | 2.6049 | 2.5615 | 3.1699 | 3.1369 | 3.1054 | 3.0739 | 3.0407 | 3.0111 | 2.9959 | 2.9839 | 2.9715 | 2.959 | 2.9468 | 2.9354 | 2.925 | 2.9158 | 2.9075 | 2.9001 | 2.8933 | 2.8867 | 2.8857 | 2.8775 | 2.8718 | 2.8661 | 2.8604 | 2.8547
Gladstone | Medium | 2.946 | 2.8095 | 2.7289 | 2.7858 | 2.8207 | 2.8044 | 2.7857 | 2.7637 | 2.737 | 2.7115 | 2.6859 | 2.6588 | 2.6344 | 2.6219 | 2.6122 | 2.6022 | 2.5921 | 2.5822 | 2.573 | 2.5645 | 2.5569 | 2.5502 | 2.5441 | 2.5385 | 2.5331 | 2.5326 | 2.5259 | 2.5213 | 2.5167 | 2.5121 | 2.5075
Hazelwood | Medium | 0.08905 | 0.090831 | 0.092648 | 0.094501 | 0.096391 | 0.098319 | 0.10029 | 0.10229 | 0.10434 | 0.10642 | 0.10855 | 0.11072 | 0.11294 | 0.1152 | 0.1175 | 0.11985 | 0.12225 | 0.12469 | 0.12719 | 0.12973 | 0.13232 | 0.13497 | 0.13767 | 0.14042 | 0.14323 | 0.1461 | 0.14882 | 0.1516 | 0.15439 | 0.15717 | 0.15995
Kogan Creek | Medium | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904 | 0.82904
Loy Yang A | Medium | 0.08905 | 0.090831 | 0.092648 | 0.094501 | 0.096391 | 0.098319 | 0.10029 | 0.10229 | 0.10434 | 0.10642 | 0.10855 | 0.11072 | 0.11294 | 0.1152 | 0.1175 | 0.11985 | 0.12225 | 0.12469 | 0.12719 | 0.12973 | 0.13232 | 0.13497 | 0.13767 | 0.14042 | 0.14323 | 0.1461 | 0.14882 | 0.1516 | 0.15439 | 0.15717 | 0.15995
Loy Yang B | Medium | 0.39578 | 0.39974 | 0.40373 | 0.40777 | 0.41185 | 0.41597 | 0.42013 | 0.42433 | 0.42857 | 0.43286 | 0.43719 | 0.44156 | 0.44597 | 0.45043 | 0.45494 | 0.45949 | 0.46408 | 0.46872 | 0.47341 | 0.47814 | 0.48293 | 0.48776 | 0.49263 | 0.49756 | 0.50253 | 0.50756 | 0.51246 | 0.51741 | 0.52236 | 0.52732 | 0.53227
Macquarie Generation | Medium | 1.63 | 1.6655 | 1.705 | 1.8241 | 1.9195 | 1.9743 | 2.006 | 2.0062 | 1.9997 | 1.9896 | 2.0079 | 2.1346 | 2.6243 | 2.6108 | 2.5999 | 2.5887 | 2.5774 | 2.5665 | 2.5563 | 2.547 | 2.5387 | 2.5314 | 2.5247 | 2.5186 | 2.5127 | 2.5117 | 2.5044 | 2.4993 | 2.4942 | 2.489 | 2.4839
Millmerran | Medium | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957 | 0.93957
Northern | Medium | 1.6425 | 1.6753 | 1.7088 | 1.743 | 2.2935 | 2.3393 | 2.3861 | 2.4338 | 2.4825 | 2.5322 | 2.5828 | 2.6345 | 2.6872 | 2.7409 | 2.7957 | 2.8516 | 2.9087 | 2.9668 | 3.0262 | 3.0867 | 3.1484 | 3.2114 | 3.2756 | 3.3411 | 3.408 | 3.4761 | 3.541 | 3.6072 | 3.6733 | 3.7395 | 3.8057
Redbank | Medium | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
Stanwell | Medium | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 1.5443 | 2.3788 | 2.3666 | 2.3569 | 2.3468 | 2.3367 | 2.3268 | 2.3177 | 2.3093 | 2.3018 | 2.2952 | 2.2892 | 2.2836 | 2.2783 | 2.2775 | 2.2709 | 2.2663 | 2.2616 | 2.257 | 2.2524
Tarong | Medium | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Yallourn | Medium | 0.098945 | 0.10092 | 0.10294 | 0.105 | 0.1071 | 0.10924 | 0.11143 | 0.11366 | 0.11593 | 0.11825 | 0.12061 | 0.12303 | 0.12549 | 0.128 | 0.13056 | 0.13317 | 0.13583 | 0.13855 | 0.14132 | 0.14414 | 0.14703 | 0.14997 | 0.15297 | 0.15603 | 0.15915 | 0.16233 | 0.16536 | 0.16845 | 0.17154 | 0.17463 | 0.17772
Condamine | Medium | 4.5178 | 6.144 | 7.4076 | 7.3387 | 7.3396 | 7.7255 | 8.0096 | 8.146 | 8.2418 | 8.2455 | 8.3504 | 8.4482 | 8.4407 | 8.4335 | 8.4647 | 8.4999 | 8.6968 | 8.8938 | 8.8946 | 8.8953 | 8.8962 | 8.8981 | 8.944 | 9.1432 | 9.3433 | 9.3886 | 9.3886 | 9.3886 | 9.3886 | 9.3886 | 9.3886
Darling Downs | Medium | 4.5178 | 6.144 | 7.4076 | 7.3387 | 7.3396 | 7.7255 | 8.0096 | 8.146 | 8.2418 | 8.2455 | 8.3504 | 8.4482 | 8.4407 | 8.4335 | 8.4647 | 8.4999 | 8.6968 | 8.8938 | 8.8946 | 8.8953 | 8.8962 | 8.8981 | 8.944 | 9.1432 | 9.3433 | 9.3886 | 9.3886 | 9.3886 | 9.3886 | 9.3886 | 9.3886
Osborne | Medium | 4.9074 | 5.6332 | 6.4668 | 6.6271 | 6.6913 | 7.075 | 7.5103 | 7.7928 | 7.8622 | 7.9206 | 8.1186 | 8.3009 | 8.4869 | 8.7275 | 8.9968 | 9.2007 | 9.2274 | 9.2354 | 9.2893 | 9.5827 | 9.825 | 9.855 | 9.996 | 10.1196 | 10.1614 | 10.1966 | 10.1966 | 10.1966 | 10.1966 | 10.1966 | 10.1966
Pelican Point | Medium | 4.9074 | 5.6332 | 6.4668 | 6.6271 | 6.6913 | 7.075 | 7.5103 | 7.7928 | 7.8622 | 7.9206 | 8.1186 | 8.3009 | 8.4869 | 8.7275 | 8.9968 | 9.2007 | 9.2274 | 9.2354 | 9.2893 | 9.5827 | 9.825 | 9.855 | 9.996 | 10.1196 | 10.1614 | 10.1966 | 10.1966 | 10.1966 | 10.1966 | 10.1966 | 10.1966
Swanbank E | Medium | 4.8033 | 6.6314 | 7.9647 | 7.8908 | 7.8902 | 8.2055 | 8.5563 | 8.6912 | 8.7175 | 8.7196 | 8.8231 | 8.9195 | 8.9106 | 8.9018 | 8.9316 | 8.9654 | 9.1609 | 9.3565 | 9.3558 | 9.3551 | 9.3546 | 9.3502 | 9.385 | 9.5734 | 9.7631 | 9.8032 | 9.8032 | 9.8032 | 9.8032 | 9.8032 | 9.8032
Tallawarra | Medium | 5.8444 | 6.892 | 7.3401 | 7.1729 | 7.128 | 7.5085 | 7.941 | 8.2209 | 8.2877 | 8.3429 | 8.5151 | 8.6944 | 8.8115 | 8.9607 | 9.2273 | 9.4282 | 9.4521 | 9.4578 | 9.5088 | 9.7992 | 10.039 | 10.0653 | 10.2012 | 10.3903 | 10.496 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271
Tamar Valley CCGT | Medium | 4.8051 | 5.5376 | 6.3778 | 6.5447 | 6.6155 | 7.0056 | 7.4475 | 7.7364 | 7.8122 | 7.877 | 8.0591 | 8.2476 | 8.3737 | 8.532 | 8.8074 | 9.0175 | 9.0503 | 9.0643 | 9.1242 | 9.4236 | 9.6719 | 9.7066 | 9.8513 | 10.0489 | 10.163 | 10.1983 | 10.1983 | 10.1983 | 10.1983 | 10.1983 | 10.1983
Townsville | Medium | 5.9218 | 5.9175 | 5.9133 | 6.2452 | 6.5773 | 6.941 | 7.3048 | 7.3006 | 7.2964 | 7.2923 | 7.2882 | 7.2841 | 7.2801 | 7.276 | 7.272 | 7.268 | 7.264 | 7.2601 | 7.2561 | 7.2522 | 7.2483 | 7.2366 | 7.2175 | 7.1989 | 7.1806 | 7.1716 | 7.1716 | 7.1716 | 7.1716 | 7.1716 | 7.1716
Smithfield | Medium | 5.8444 | 6.892 | 7.3401 | 7.1729 | 7.128 | 7.5085 | 7.941 | 8.2209 | 8.2877 | 8.3429 | 8.5151 | 8.6944 | 8.8115 | 8.9607 | 9.2273 | 9.4282 | 9.4521 | 9.4578 | 9.5088 | 9.7992 | 10.039 | 10.0653 | 10.2012 | 10.3903 | 10.496 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271
Yarwun | Medium | 5.2282 | 7.136 | 8.1957 | 7.9212 | 7.9266 | 8.2478 | 8.6042 | 8.7446 | 8.7762 | 8.7835 | 8.8918 | 8.993 | 8.9886 | 8.9842 | 9.0183 | 9.0561 | 9.2556 | 9.4549 | 9.4579 | 9.4608 | 9.462 | 9.4565 | 9.4888 | 9.54 | 9.5959 | 9.6382 | 9.6382 | 9.6382 | 9.6382 | 9.6382 | 9.6382
Bairnsdale | Medium | 5.9005 | 6.633 | 7.4733 | 7.6402 | 7.7109 | 8.1011 | 8.5429 | 8.8319 | 8.9077 | 8.9724 | 9.1545 | 9.343 | 9.4691 | 9.6274 | 9.9028 | 10.113 | 10.1458 | 10.1598 | 10.2197 | 10.519 | 10.7673 | 10.8131 | 10.9796 | 11.1984 | 11.3333 | 11.3788 | 11.3788 | 11.3788 | 11.3788 | 11.3788 | 11.3788
Barcaldine | Medium | 7.2282 | 9.136 | 10.1957 | 9.9212 | 9.9266 | 10.2478 | 10.6042 | 10.7446 | 10.7762 | 10.7835 | 10.8918 | 10.993 | 10.9886 | 10.9842 | 11.0183 | 11.0561 | 11.2556 | 11.4549 | 11.4579 | 11.4608 | 11.462 | 11.4565 | 11.4888 | 11.54 | 11.5959 | 11.6382 | 11.6382 | 11.6382 | 11.6382 | 11.6382 | 11.6382
Bell Bay Three | Medium | 6.8051 | 7.5376 | 8.3778 | 8.5447 | 8.6155 | 9.0056 | 9.4475 | 9.7364 | 9.8122 | 9.877 | 10.0591 | 10.2476 | 10.3737 | 10.532 | 10.8074 | 11.0175 | 11.0503 | 11.0643 | 11.1242 | 11.4236 | 11.6719 | 11.7066 | 11.8513 | 12.0489 | 12.163 | 12.1983 | 12.1983 | 12.1983 | 12.1983 | 12.1983 | 12.1983
Braemar | Medium | 6.5178 | 8.144 | 9.4076 | 9.3387 | 9.3396 | 9.7255 | 10.0096 | 10.146 | 10.2418 | 10.2455 | 10.3504 | 10.4482 | 10.4407 | 10.4335 | 10.4647 | 10.4999 | 10.6968 | 10.8938 | 10.8946 | 10.8953 | 10.8962 | 10.8981 | 10.944 | 11.1432 | 11.3433 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886
Braemar 2 | Medium | 6.5178 | 8.144 | 9.4076 | 9.3387 | 9.3396 | 9.7255 | 10.0096 | 10.146 | 10.2418 | 10.2455 | 10.3504 | 10.4482 | 10.4407 | 10.4335 | 10.4647 | 10.4999 | 10.6968 | 10.8938 | 10.8946 | 10.8953 | 10.8962 | 10.8981 | 10.944 | 11.1432 | 11.3433 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886
Colongra | Medium | 7.8444 | 8.892 | 9.3401 | 9.1729 | 9.128 | 9.5085 | 9.941 | 10.2209 | 10.2877 | 10.3429 | 10.5151 | 10.6944 | 10.8115 | 10.9607 | 11.2273 | 11.4282 | 11.4521 | 11.4578 | 11.5088 | 11.7992 | 12.039 | 12.0653 | 12.2012 | 12.3903 | 12.496 | 12.5271 | 12.5271 | 12.5271 | 12.5271 | 12.5271 | 12.5271
Dry Creek | Medium | 6.9074 | 7.6332 | 8.4668 | 8.6271 | 8.6913 | 9.075 | 9.5103 | 9.7928 | 9.8622 | 9.9206 | 10.1186 | 10.3009 | 10.4869 | 10.7275 | 10.9968 | 11.2007 | 11.2274 | 11.2354 | 11.2893 | 11.5827 | 11.825 | 11.855 | 11.996 | 12.1196 | 12.1614 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966
Hallett | Medium | 7.4951 | 8.7667 | 9.3863 | 9.3127 | 9.3124 | 10.1844 | 11.2033 | 11.4722 | 11.5177 | 11.5135 | 11.6106 | 11.7008 | 11.6856 | 11.6707 | 11.6944 | 11.7221 | 11.9116 | 12.1011 | 12.0945 | 12.088 | 12.0816 | 12.0655 | 12.0828 | 12.1196 | 12.1614 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966
Jeeralang | Medium | 5.9005 | 6.633 | 7.4733 | 7.6402 | 7.7109 | 8.1011 | 8.5429 | 8.8319 | 8.9077 | 8.9724 | 9.1545 | 9.343 | 9.4691 | 9.6274 | 9.9028 | 10.113 | 10.1458 | 10.1598 | 10.2197 | 10.519 | 10.7673 | 10.8131 | 10.9796 | 11.1984 | 11.3333 | 11.3788 | 11.3788 | 11.3788 | 11.3788 | 11.3788 | 11.3788
Ladbroke Grove | Medium | 7.0854 | 7.8103 | 8.6431 | 8.8025 | 8.8659 | 9.2487 | 9.6832 | 9.9649 | 10.0334 | 10.0909 | 10.2881 | 10.4695 | 10.6547 | 10.8945 | 11.163 | 11.3662 | 11.392 | 11.3992 | 11.4523 | 11.7449 | 11.9865 | 12.0141 | 12.1513 | 12.271 | 12.3091 | 12.3426 | 12.3426 | 12.3426 | 12.3426 | 12.3426 | 12.3426
Laverton North | Medium | 6.3221 | 7.0545 | 7.8948 | 8.0617 | 8.1324 | 8.5226 | 8.9644 | 9.2534 | 9.3292 | 9.3939 | 9.576 | 9.7645 | 9.8906 | 10.0489 | 10.3244 | 10.5345 | 10.5673 | 10.5813 | 10.6412 | 10.9405 | 11.1889 | 11.2295 | 11.3858 | 11.5947 | 11.7199 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607
Mintaro | Medium | 7.4951 | 8.7667 | 9.3863 | 9.3127 | 9.3124 | 10.1844 | 11.2033 | 11.4722 | 11.5177 | 11.5135 | 11.6106 | 11.7008 | 11.6856 | 11.6707 | 11.6944 | 11.7221 | 11.9116 | 12.1011 | 12.0945 | 12.088 | 12.0816 | 12.0655 | 12.0828 | 12.1196 | 12.1614 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966
Mortlake OCGT | Medium | 6.3221 | 7.0545 | 7.8948 | 8.0617 | 8.1324 | 8.5226 | 8.9644 | 9.2534 | 9.3292 | 9.3939 | 9.576 | 9.7645 | 9.8906 | 10.0489 | 10.3244 | 10.5345 | 10.5673 | 10.5813 | 10.6412 | 10.9405 | 11.1889 | 11.2295 | 11.3858 | 11.5947 | 11.7199 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607
Newport | Medium | 6.3221 | 7.0545 | 7.8948 | 8.0617 | 8.1324 | 8.5226 | 8.9644 | 9.2534 | 9.3292 | 9.3939 | 9.576 | 9.7645 | 9.8906 | 10.0489 | 10.3244 | 10.5345 | 10.5673 | 10.5813 | 10.6412 | 10.9405 | 11.1889 | 11.2295 | 11.3858 | 11.5947 | 11.7199 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607
Oakey | Medium | 6.5178 | 8.144 | 9.4076 | 9.3387 | 9.3396 | 9.7255 | 10.0096 | 10.146 | 10.2418 | 10.2455 | 10.3504 | 10.4482 | 10.4407 | 10.4335 | 10.4647 | 10.4999 | 10.6968 | 10.8938 | 10.8946 | 10.8953 | 10.8962 | 10.8981 | 10.944 | 11.1432 | 11.3433 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886
Quarantine | Medium | 6.9074 | 7.6332 | 8.4668 | 8.6271 | 8.6913 | 9.075 | 9.5103 | 9.7928 | 9.8622 | 9.9206 | 10.1186 | 10.3009 | 10.4869 | 10.7275 | 10.9968 | 11.2007 | 11.2274 | 11.2354 | 11.2893 | 11.5827 | 11.825 | 11.855 | 11.996 | 12.1196 | 12.1614 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966
Roma | Medium | 6.5178 | 8.144 | 9.4076 | 9.3387 | 9.3396 | 9.7255 | 10.0096 | 10.146 | 10.2418 | 10.2455 | 10.3504 | 10.4482 | 10.4407 | 10.4335 | 10.4647 | 10.4999 | 10.6968 | 10.8938 | 10.8946 | 10.8953 | 10.8962 | 10.8981 | 10.944 | 11.1432 | 11.3433 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886
Somerton | Medium | 6.3221 | 7.0545 | 7.8948 | 8.0617 | 8.1324 | 8.5226 | 8.9644 | 9.2534 | 9.3292 | 9.3939 | 9.576 | 9.7645 | 9.8906 | 10.0489 | 10.3244 | 10.5345 | 10.5673 | 10.5813 | 10.6412 | 10.9405 | 11.1889 | 11.2295 | 11.3858 | 11.5947 | 11.7199 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607
Tamar Valley OCGT | Medium | 6.8051 | 7.5376 | 8.3778 | 8.5447 | 8.6155 | 9.0056 | 9.4475 | 9.7364 | 9.8122 | 9.877 | 10.0591 | 10.2476 | 10.3737 | 10.532 | 10.8074 | 11.0175 | 11.0503 | 11.0643 | 11.1242 | 11.4236 | 11.6719 | 11.7066 | 11.8513 | 12.0489 | 12.163 | 12.1983 | 12.1983 | 12.1983 | 12.1983 | 12.1983 | 12.1983
Torrens Island | Medium | 6.9074 | 7.6332 | 8.4668 | 8.6271 | 8.6913 | 9.075 | 9.5103 | 9.7928 | 9.8622 | 9.9206 | 10.1186 | 10.3009 | 10.4869 | 10.7275 | 10.9968 | 11.2007 | 11.2274 | 11.2354 | 11.2893 | 11.5827 | 11.825 | 11.855 | 11.996 | 12.1196 | 12.1614 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966
Uranquinty | Medium | 7.6223 | 8.3809 | 9.2177 | 9.381 | 9.4482 | 9.8349 | 10.2733 | 10.5588 | 10.6312 | 10.6925 | 10.8712 | 11.0563 | 11.179 | 11.3339 | 11.6061 | 11.8128 | 11.8423 | 11.853 | 11.9096 | 12.2057 | 12.4508 | 12.4744 | 12.5737 | 12.6565 | 12.6852 | 12.714 | 12.714 | 12.714 | 12.714 | 12.714 | 12.714
Valley Power | Medium | 5.9005 | 6.633 | 7.4733 | 7.6402 | 7.7109 | 8.1011 | 8.5429 | 8.8319 | 8.9077 | 8.9724 | 9.1545 | 9.343 | 9.4691 | 9.6274 | 9.9028 | 10.113 | 10.1458 | 10.1598 | 10.2197 | 10.519 | 10.7673 | 10.8131 | 10.9796 | 11.1984 | 11.3333 | 11.3788 | 11.3788 | 11.3788 | 11.3788 | 11.3788 | 11.3788
Condamine | High | 3.5821 | 5.2548 | 6.7065 | 6.2666 | 5.8886 | 6.0753 | 6.4468 | 6.712 | 6.5977 | 6.473 | 6.4739 | 6.5599 | 6.8747 | 7.1229 | 7.1422 | 7.1517 | 7.3024 | 7.4766 | 7.5415 | 7.5718 | 7.57 | 7.5732 | 7.6771 | 7.8038 | 7.8307 | 7.8314 | 7.8314 | 7.8314 | 7.8314 | 7.8314 | 7.8314
Darling Downs | High | 3.5821 | 5.2548 | 6.7065 | 6.2666 | 5.8886 | 6.0753 | 6.4468 | 6.712 | 6.5977 | 6.473 | 6.4739 | 6.5599 | 6.8747 | 7.1229 | 7.1422 | 7.1517 | 7.3024 | 7.4766 | 7.5415 | 7.5718 | 7.57 | 7.5732 | 7.6771 | 7.8038 | 7.8307 | 7.8314 | 7.8314 | 7.8314 | 7.8314 | 7.8314 | 7.8314
Osborne | High | 4.5155 | 5.3527 | 6.1915 | 5.991 | 5.9878 | 6.4522 | 6.9977 | 7.2715 | 7.2651 | 7.2587 | 7.3957 | 7.6219 | 7.7525 | 7.7962 | 7.8143 | 7.8341 | 7.9509 | 8.1492 | 8.2285 | 8.2225 | 8.2165 | 8.2651 | 8.4284 | 8.5363 | 8.5819 | 8.6314 | 8.6314 | 8.6314 | 8.6314 | 8.6314 | 8.6314
Pelican Point | High | 4.5155 | 5.3527 | 6.1915 | 5.991 | 5.9878 | 6.4522 | 6.9977 | 7.2715 | 7.2651 | 7.2587 | 7.3957 | 7.6219 | 7.7525 | 7.7962 | 7.8143 | 7.8341 | 7.9509 | 8.1492 | 8.2285 | 8.2225 | 8.2165 | 8.2651 | 8.4284 | 8.5363 | 8.5819 | 8.6314 | 8.6314 | 8.6314 | 8.6314 | 8.6314 | 8.6314
Swanbank E | High | 3.8676 | 5.7422 | 7.333 | 6.8881 | 6.4392 | 6.5553 | 6.9934 | 7.2572 | 7.0733 | 6.9472 | 6.9466 | 7.0311 | 7.3445 | 7.5913 | 7.6091 | 7.6172 | 7.7664 | 7.9393 | 8.0027 | 8.0316 | 8.0284 | 8.0253 | 8.1181 | 8.2059 | 8.2184 | 8.2381 | 8.2381 | 8.2381 | 8.2381 | 8.2381 | 8.2381
Tallawarra | High | 5.1616 | 6.0549 | 6.7606 | 6.4983 | 6.4246 | 6.8857 | 7.4284 | 7.6996 | 7.6906 | 7.681 | 7.8144 | 8.0376 | 8.1655 | 8.2063 | 8.2218 | 8.2385 | 8.264 | 8.3773 | 8.5198 | 8.5714 | 8.5629 | 8.5416 | 8.6336 | 8.7364 | 8.7879 | 8.846 | 8.846 | 8.846 | 8.846 | 8.846 | 8.846
Tamar Valley CCGT | High | 4.4132 | 5.2571 | 6.1025 | 5.9086 | 5.912 | 6.3828 | 6.9349 | 7.2151 | 7.2151 | 7.2151 | 7.3584 | 7.5908 | 7.7277 | 7.7775 | 7.8019 | 7.8278 | 7.8622 | 7.9838 | 8.1352 | 8.1958 | 8.1958 | 8.1829 | 8.2837 | 8.395 | 8.455 | 8.5172 | 8.5172 | 8.5172 | 8.5172 | 8.5172 | 8.5172
Townsville | High | 4.9131 | 4.9088 | 4.9046 | 4.9003 | 4.8961 | 4.8919 | 4.8877 | 4.8836 | 4.8794 | 4.9911 | 5.1028 | 5.4349 | 6.3274 | 6.9025 | 6.9171 | 6.9222 | 7.0684 | 7.2381 | 7.2986 | 7.3245 | 7.3182 | 7.3088 | 7.392 | 7.4985 | 7.5056 | 7.4966 | 7.4966 | 7.4966 | 7.4966 | 7.4966 | 7.4966
Smithfield | High | 5.1616 | 6.0549 | 6.7606 | 6.4983 | 6.4246 | 6.8857 | 7.4284 | 7.6996 | 7.6906 | 7.681 | 7.8144 | 8.0376 | 8.1655 | 8.2063 | 8.2218 | 8.2385 | 8.264 | 8.3773 | 8.5198 | 8.5714 | 8.5629 | 8.5416 | 8.6336 | 8.7364 | 8.7879 | 8.846 | 8.846 | 8.846 | 8.846 | 8.846 | 8.846
Yarwun | High | 4.2926 | 6.2467 | 7.5641 | 6.9185 | 6.4757 | 6.5976 | 7.0414 | 7.3106 | 7.132 | 7.011 | 7.0153 | 7.1046 | 7.2719 | 7.373 | 7.3966 | 7.4102 | 7.5649 | 7.7429 | 7.8114 | 7.8453 | 7.8453 | 7.8453 | 7.9425 | 8.0346 | 8.0512 | 8.073 | 8.073 | 8.073 | 8.073 | 8.073 | 8.073
Bairnsdale | High | 5.5086 | 6.3525 | 7.198 | 7.004 | 7.0074 | 7.4783 | 8.0303 | 8.3105 | 8.3105 | 8.3105 | 8.4539 | 8.6863 | 8.8231 | 8.873 | 8.8973 | 8.9232 | 8.9577 | 9.0793 | 9.2307 | 9.2912 | 9.2912 | 9.2894 | 9.412 | 9.5446 | 9.6253 | 9.6977 | 9.6977 | 9.6977 | 9.6977 | 9.6977 | 9.6977
Barcaldine | High | 6.2926 | 8.2467 | 9.5641 | 8.9185 | 8.4757 | 8.5976 | 9.0414 | 9.3106 | 9.132 | 9.011 | 9.0153 | 9.1046 | 9.2719 | 9.373 | 9.3966 | 9.4102 | 9.5649 | 9.7429 | 9.8114 | 9.8453 | 9.8453 | 9.8453 | 9.9425 | 10.0346 | 10.0512 | 10.073 | 10.073 | 10.073 | 10.073 | 10.073 | 10.073
Bell Bay Three | High | 6.4132 | 7.2571 | 8.1025 | 7.9086 | 7.912 | 8.3828 | 8.9349 | 9.2151 | 9.2151 | 9.2151 | 9.3584 | 9.5908 | 9.7277 | 9.7775 | 9.8019 | 9.8278 | 9.8622 | 9.9838 | 10.1352 | 10.1958 | 10.1958 | 10.1829 | 10.2837 | 10.395 | 10.455 | 10.5172 | 10.5172 | 10.5172 | 10.5172 | 10.5172 | 10.5172
Braemar | High | 5.5821 | 7.2548 | 8.7065 | 8.2666 | 7.8886 | 8.0753 | 8.4468 | 8.712 | 8.5977 | 8.473 | 8.4739 | 8.5599 | 8.8747 | 9.1229 | 9.1422 | 9.1517 | 9.3024 | 9.4766 | 9.5415 | 9.5718 | 9.57 | 9.5732 | 9.6771 | 9.8038 | 9.8307 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314
Braemar 2 | High | 5.5821 | 7.2548 | 8.7065 | 8.2666 | 7.8886 | 8.0753 | 8.4468 | 8.712 | 8.5977 | 8.473 | 8.4739 | 8.5599 | 8.8747 | 9.1229 | 9.1422 | 9.1517 | 9.3024 | 9.4766 | 9.5415 | 9.5718 | 9.57 | 9.5732 | 9.6771 | 9.8038 | 9.8307 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314
Colongra | High | 7.1616 | 8.0549 | 8.7606 | 8.4983 | 8.4246 | 8.8857 | 9.4284 | 9.6996 | 9.6906 | 9.681 | 9.8144 | 10.0376 | 10.1655 | 10.2063 | 10.2218 | 10.2385 | 10.264 | 10.3773 | 10.5198 | 10.5714 | 10.5629 | 10.5416 | 10.6336 | 10.7364 | 10.7879 | 10.846 | 10.846 | 10.846 | 10.846 | 10.846 | 10.846
Dry Creek | High | 6.5155 | 7.3527 | 8.1915 | 7.991 | 7.9878 | 8.4522 | 8.9977 | 9.2715 | 9.2651 | 9.2587 | 9.3957 | 9.6219 | 9.7525 | 9.7962 | 9.8143 | 9.8341 | 9.9509 | 10.1492 | 10.2285 | 10.2225 | 10.2165 | 10.2651 | 10.4284 | 10.5363 | 10.5819 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314
Hallett | High | 6.8122 | 7.8775 | 8.7547 | 8.31 | 8.0544 | 8.6799 | 9.6187 | 10.0637 | 9.8735 | 9.7411 | 9.7341 | 9.8124 | 9.9688 | 10.0595 | 10.0727 | 10.0762 | 10.2209 | 10.3891 | 10.448 | 10.4725 | 10.4648 | 10.4543 | 10.5366 | 10.6141 | 10.6167 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314
Jeeralang | High | 5.5086 | 6.3525 | 7.198 | 7.004 | 7.0074 | 7.4783 | 8.0303 | 8.3105 | 8.3105 | 8.3105 | 8.4539 | 8.6863 | 8.8231 | 8.873 | 8.8973 | 8.9232 | 8.9577 | 9.0793 | 9.2307 | 9.2912 | 9.2912 | 9.2894 | 9.412 | 9.5446 | 9.6253 | 9.6977 | 9.6977 | 9.6977 | 9.6977 | 9.6977 | 9.6977
Ladbroke Grove | High | 6.6935 | 7.5298 | 8.3678 | 8.1664 | 8.1624 | 8.6259 | 9.1706 | 9.4435 | 9.4363 | 9.4291 | 9.5652 | 9.7905 | 9.9203 | 9.9632 | 9.9806 | 9.9995 | 10.1154 | 10.313 | 10.3915 | 10.3847 | 10.378 | 10.4242 | 10.5837 | 10.6877 | 10.7296 | 10.7774 | 10.7774 | 10.7774 | 10.7774 | 10.7774 | 10.7774
Laverton North | High | 5.9302 | 6.774 | 7.6195 | 7.4255 | 7.4289 | 7.8998 | 8.4519 | 8.732 | 8.732 | 8.732 | 8.8754 | 9.1078 | 9.2446 | 9.2945 | 9.3188 | 9.3448 | 9.3792 | 9.5008 | 9.6522 | 9.7127 | 9.7127 | 9.7058 | 9.8182 | 9.9409 | 10.0119 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795
Mintaro | High | 6.8122 | 7.8775 | 8.7547 | 8.31 | 8.0544 | 8.6799 | 9.6187 | 10.0637 | 9.8735 | 9.7411 | 9.7341 | 9.8124 | 9.9688 | 10.0595 | 10.0727 | 10.0762 | 10.2209 | 10.3891 | 10.448 | 10.4725 | 10.4648 | 10.4543 | 10.5366 | 10.6141 | 10.6167 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314
Mortlake OCGT | High | 5.9302 | 6.774 | 7.6195 | 7.4255 | 7.4289 | 7.8998 | 8.4519 | 8.732 | 8.732 | 8.732 | 8.8754 | 9.1078 | 9.2446 | 9.2945 | 9.3188 | 9.3448 | 9.3792 | 9.5008 | 9.6522 | 9.7127 | 9.7127 | 9.7058 | 9.8182 | 9.9409 | 10.0119 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795
Newport | High | 5.9302 | 6.774 | 7.6195 | 7.4255 | 7.4289 | 7.8998 | 8.4519 | 8.732 | 8.732 | 8.732 | 8.8754 | 9.1078 | 9.2446 | 9.2945 | 9.3188 | 9.3448 | 9.3792 | 9.5008 | 9.6522 | 9.7127 | 9.7127 | 9.7058 | 9.8182 | 9.9409 | 10.0119 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795
Oakey | High | 5.5821 | 7.2548 | 8.7065 | 8.2666 | 7.8886 | 8.0753 | 8.4468 | 8.712 | 8.5977 | 8.473 | 8.4739 | 8.5599 | 8.8747 | 9.1229 | 9.1422 | 9.1517 | 9.3024 | 9.4766 | 9.5415 | 9.5718 | 9.57 | 9.5732 | 9.6771 | 9.8038 | 9.8307 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314
Quarantine | High | 6.5155 | 7.3527 | 8.1915 | 7.991 | 7.9878 | 8.4522 | 8.9977 | 9.2715 | 9.2651 | 9.2587 | 9.3957 | 9.6219 | 9.7525 | 9.7962 | 9.8143 | 9.8341 | 9.9509 | 10.1492 | 10.2285 | 10.2225 | 10.2165 | 10.2651 | 10.4284 | 10.5363 | 10.5819 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314
Roma | High | 5.5821 | 7.2548 | 8.7065 | 8.2666 | 7.8886 | 8.0753 | 8.4468 | 8.712 | 8.5977 | 8.473 | 8.4739 | 8.5599 | 8.8747 | 9.1229 | 9.1422 | 9.1517 | 9.3024 | 9.4766 | 9.5415 | 9.5718 | 9.57 | 9.5732 | 9.6771 | 9.8038 | 9.8307 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314
Somerton | High | 5.9302 | 6.774 | 7.6195 | 7.4255 | 7.4289 | 7.8998 | 8.4519 | 8.732 | 8.732 | 8.732 | 8.8754 | 9.1078 | 9.2446 | 9.2945 | 9.3188 | 9.3448 | 9.3792 | 9.5008 | 9.6522 | 9.7127 | 9.7127 | 9.7058 | 9.8182 | 9.9409 | 10.0119 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795
Tamar Valley OCGT | High | 6.4132 | 7.2571 | 8.1025 | 7.9086 | 7.912 | 8.3828 | 8.9349 | 9.2151 | 9.2151 | 9.2151 | 9.3584 | 9.5908 | 9.7277 | 9.7775 | 9.8019 | 9.8278 | 9.8622 | 9.9838 | 10.1352 | 10.1958 | 10.1958 | 10.1829 | 10.2837 | 10.395 | 10.455 | 10.5172 | 10.5172 | 10.5172 | 10.5172 | 10.5172 | 10.5172
Torrens Island | High | 6.5155 | 7.3527 | 8.1915 | 7.991 | 7.9878 | 8.4522 | 8.9977 | 9.2715 | 9.2651 | 9.2587 | 9.3957 | 9.6219 | 9.7525 | 9.7962 | 9.8143 | 9.8341 | 9.9509 | 10.1492 | 10.2285 | 10.2225 | 10.2165 | 10.2651 | 10.4284 | 10.5363 | 10.5819 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314
Uranquinty | High | 7.2304 | 8.1004 | 8.9424 | 8.6987 | 8.6486 | 9.1621 | 9.7607 | 10.0374 | 10.034 | 10.0306 | 10.1705 | 10.3894 | 10.5228 | 10.5795 | 10.6005 | 10.6231 | 10.6542 | 10.7725 | 10.9206 | 10.9779 | 10.9746 | 10.9507 | 11.0327 | 11.1258 | 11.1316 | 11.1488 | 11.1488 | 11.1488 | 11.1488 | 11.1488 | 11.1488
Valley Power | High | 5.5086 | 6.3525 | 7.198 | 7.004 | 7.0074 | 7.4783 | 8.0303 | 8.3105 | 8.3105 | 8.3105 | 8.4539 | 8.6863 | 8.8231 | 8.873 | 8.8973 | 8.9232 | 8.9577 | 9.0793 | 9.2307 | 9.2912 | 9.2912 | 9.2894 | 9.412 | 9.5446 | 9.6253 | 9.6977 | 9.6977 | 9.6977 | 9.6977 | 9.6977 | 9.6977
Condamine | Low | 5.9017 | 8.1707 | 9.9976 | 10.7001 | 11.2954 | 11.5795 | 11.5906 | 11.6599 | 11.7289 | 11.7298 | 11.7306 | 11.7314 | 11.7323 | 11.7498 | 11.7818 | 11.7971 | 11.9145 | 12.0312 | 12.0306 | 12.03 | 12.0294 | 12.0271 | 12.0231 | 12.0193 | 12.0155 | 12.0136 | 12.0136 | 12.0136 | 12.0136 | 12.0136 | 12.0136
Darling Downs | Low | 5.9017 | 8.1707 | 9.9976 | 10.7001 | 11.2954 | 11.5795 | 11.5906 | 11.6599 | 11.7289 | 11.7298 | 11.7306 | 11.7314 | 11.7323 | 11.7498 | 11.7818 | 11.7971 | 11.9145 | 12.0312 | 12.0306 | 12.03 | 12.0294 | 12.0271 | 12.0231 | 12.0193 | 12.0155 | 12.0136 | 12.0136 | 12.0136 | 12.0136 | 12.0136 | 12.0136
Osborne | Low | 5.8112 | 6.5903 | 7.5736 | 7.8591 | 8.2782 | 9.0314 | 9.5573 | 9.953 | 10.3433 | 10.8259 | 11.3238 | 11.5215 | 11.5783 | 11.6315 | 11.6866 | 11.9494 | 12.2954 | 12.5984 | 12.9045 | 13.1013 | 13.1562 | 13.1552 | 13.244 | 13.3143 | 13.2791 | 13.2616 | 13.2616 | 13.2616 | 13.2616 | 13.2616 | 13.2616
Pelican Point | Low | 5.8112 | 6.5903 | 7.5736 | 7.8591 | 8.2782 | 9.0314 | 9.5573 | 9.953 | 10.3433 | 10.8259 | 11.3238 | 11.5215 | 11.5783 | 11.6315 | 11.6866 | 11.9494 | 12.2954 | 12.5984 | 12.9045 | 13.1013 | 13.1562 | 13.1552 | 13.244 | 13.3143 | 13.2791 | 13.2616 | 13.2616 | 13.2616 | 13.2616 | 13.2616 | 13.2616
Swanbank E | Low | 6.1872 | 8.5681 | 10.3748 | 11.0525 | 11.6467 | 12.0384 | 12.2058 | 12.2052 | 12.2045 | 12.2039 | 12.2033 | 12.2027 | 12.2021 | 12.2181 | 12.2488 | 12.2626 | 12.3785 | 12.4939 | 12.4918 | 12.4898 | 12.4877 | 12.4791 | 12.4641 | 12.4495 | 12.4353 | 12.4282 | 12.4282 | 12.4282 | 12.4282 | 12.4282 | 12.4282
Tallawarra | Low | 6.7482 | 7.8491 | 8.6674 | 9.4298 | 10.1388 | 10.4414 | 10.6788 | 11.0509 | 11.2646 | 11.4044 | 11.6501 | 11.7604 | 11.8145 | 11.8647 | 11.9172 | 12.1769 | 12.5202 | 12.8208 | 13.0975 | 13.2096 | 13.2096 | 13.2096 | 13.2067 | 13.2007 | 13.1945 | 13.1914 | 13.1914 | 13.1914 | 13.1914 | 13.1914 | 13.1914
Tamar Valley CCGT | Low | 5.7089 | 6.4947 | 7.4846 | 7.7767 | 8.2023 | 8.9621 | 9.4944 | 9.8966 | 10.2048 | 10.6054 | 11.1096 | 11.3136 | 11.3766 | 11.436 | 11.4972 | 11.7662 | 12.1184 | 12.4273 | 12.7129 | 12.834 | 12.8425 | 12.9121 | 13.0833 | 13.215 | 13.3777 | 13.5146 | 13.5146 | 13.5146 | 13.5146 | 13.5146 | 13.5146
Townsville | Low | 6.9304 | 6.9262 | 6.9219 | 8.8827 | 10.999 | 11.1481 | 11.1416 | 11.3364 | 11.5315 | 11.5277 | 11.5239 | 11.5201 | 11.5164 | 11.5293 | 11.5568 | 11.5676 | 11.5636 | 11.5597 | 11.5557 | 11.5518 | 11.5479 | 11.5363 | 11.5171 | 11.4985 | 11.4802 | 11.4712 | 11.4712 | 11.4712 | 11.4712 | 11.4712 | 11.4712
Smithfield | Low | 6.7482 | 7.8491 | 8.6674 | 9.4298 | 10.1388 | 10.4414 | 10.6788 | 11.0509 | 11.2646 | 11.4044 | 11.6501 | 11.7604 | 11.8145 | 11.8647 | 11.9172 | 12.1769 | 12.5202 | 12.8208 | 13.0975 | 13.2096 | 13.2096 | 13.2096 | 13.2067 | 13.2007 | 13.1945 | 13.1914 | 13.1914 | 13.1914 | 13.1914 | 13.1914 | 13.1914
Yarwun | Low | 6.6122 | 9.1627 | 10.9648 | 11.5375 | 11.9584 | 12.1703 | 12.2537 | 12.2586 | 12.2633 | 12.2677 | 12.272 | 12.2762 | 12.2802 | 12.2839 | 12.2876 | 12.291 | 12.2944 | 12.2976 | 12.3006 | 12.3034 | 12.3047 | 12.2991 | 12.2885 | 12.2782 | 12.2681 | 12.2631 | 12.2631 | 12.2631 | 12.2631 | 12.2631 | 12.2631
Bairnsdale | Low | 6.8043 | 7.5901 | 8.58 | 8.8721 | 9.2977 | 10.0575 | 10.5899 | 10.992 | 11.3003 | 11.7008 | 12.205 | 12.4091 | 12.4721 | 12.5314 | 12.5927 | 12.8616 | 13.2138 | 13.5228 | 13.8083 | 13.9294 | 13.938 | 14.0185 | 14.2116 | 14.3645 | 14.548 | 14.6951 | 14.6951 | 14.6951 | 14.6951 | 14.6951 | 14.6951
Barcaldine | Low | 8.6122 | 11.1627 | 12.9648 | 13.5375 | 13.9584 | 14.1703 | 14.2537 | 14.2586 | 14.2633 | 14.2677 | 14.272 | 14.2762 | 14.2802 | 14.2839 | 14.2876 | 14.291 | 14.2944 | 14.2976 | 14.3006 | 14.3034 | 14.3047 | 14.2991 | 14.2885 | 14.2782 | 14.2681 | 14.2631 | 14.2631 | 14.2631 | 14.2631 | 14.2631 | 14.2631
Bell Bay Three | Low | 7.7089 | 8.4947 | 9.4846 | 9.7767 | 10.2023 | 10.9621 | 11.4944 | 11.8966 | 12.2048 | 12.6054 | 13.1096 | 13.3136 | 13.3766 | 13.436 | 13.4972 | 13.7662 | 14.1184 | 14.4273 | 14.7129 | 14.834 | 14.8425 | 14.9121 | 15.0833 | 15.215 | 15.3777 | 15.5146 | 15.5146 | 15.5146 | 15.5146 | 15.5146 | 15.5146
Braemar | Low | 7.9017 | 10.1707 | 11.9976 | 12.7001 | 13.2954 | 13.5795 | 13.5906 | 13.6599 | 13.7289 | 13.7298 | 13.7306 | 13.7314 | 13.7323 | 13.7498 | 13.7818 | 13.7971 | 13.9145 | 14.0312 | 14.0306 | 14.03 | 14.0294 | 14.0271 | 14.0231 | 14.0193 | 14.0155 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136
Braemar 2 | Low | 7.9017 | 10.1707 | 11.9976 | 12.7001 | 13.2954 | 13.5795 | 13.5906 | 13.6599 | 13.7289 | 13.7298 | 13.7306 | 13.7314 | 13.7323 | 13.7498 | 13.7818 | 13.7971 | 13.9145 | 14.0312 | 14.0306 | 14.03 | 14.0294 | 14.0271 | 14.0231 | 14.0193 | 14.0155 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136
Colongra | Low | 8.7482 | 9.8491 | 10.6674 | 11.4298 | 12.1388 | 12.4414 | 12.6788 | 13.0509 | 13.2646 | 13.4044 | 13.6501 | 13.7604 | 13.8145 | 13.8647 | 13.9172 | 14.1769 | 14.5202 | 14.8208 | 15.0975 | 15.2096 | 15.2096 | 15.2096 | 15.2067 | 15.2007 | 15.1945 | 15.1914 | 15.1914 | 15.1914 | 15.1914 | 15.1914 | 15.1914
Dry Creek | Low | 7.8112 | 8.5903 | 9.5736 | 9.8591 | 10.2782 | 11.0314 | 11.5573 | 11.953 | 12.3433 | 12.8259 | 13.3238 | 13.5215 | 13.5783 | 13.6315 | 13.6866 | 13.9494 | 14.2954 | 14.5984 | 14.9045 | 15.1013 | 15.1562 | 15.1552 | 15.244 | 15.3143 | 15.2791 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616
Hallett | Low | 8.3989 | 10.3132 | 11.9431 | 12.6208 | 13.3317 | 13.7147 | 13.9411 | 14.3022 | 14.51 | 14.6439 | 14.8837 | 14.984 | 14.9771 | 14.9703 | 14.9637 | 14.957 | 14.9503 | 14.9437 | 15.0509 | 15.1596 | 15.1562 | 15.1552 | 15.244 | 15.3143 | 15.2791 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616
Jeeralang | Low | 6.8043 | 7.5901 | 8.58 | 8.8721 | 9.2977 | 10.0575 | 10.5899 | 10.992 | 11.3003 | 11.7008 | 12.205 | 12.4091 | 12.4721 | 12.5314 | 12.5927 | 12.8616 | 13.2138 | 13.5228 | 13.8083 | 13.9294 | 13.938 | 14.0185 | 14.2116 | 14.3645 | 14.548 | 14.6951 | 14.6951 | 14.6951 | 14.6951 | 14.6951 | 14.6951
Ladbroke Grove | Low | 7.9892 | 8.7675 | 9.7499 | 10.0345 | 10.4527 | 11.2051 | 11.7301 | 12.125 | 12.5145 | 12.9962 | 13.4933 | 13.6902 | 13.7461 | 13.7985 | 13.8529 | 14.1148 | 14.46 | 14.7622 | 15.0675 | 15.2635 | 15.3176 | 15.3143 | 15.3992 | 15.5077 | 15.6632 | 15.7966 | 15.7966 | 15.7966 | 15.7966 | 15.7966 | 15.7966
Laverton North | Low | 7.2259 | 8.0117 | 9.0016 | 9.2937 | 9.7193 | 10.479 | 11.0114 | 11.4136 | 11.7218 | 12.1223 | 12.6265 | 12.8306 | 12.8936 | 12.9529 | 13.0142 | 13.2832 | 13.6353 | 13.9443 | 14.2299 | 14.351 | 14.3595 | 14.4349 | 14.6178 | 14.7608 | 14.9346 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769
Mintaro | Low | 8.3989 | 10.3132 | 11.9431 | 12.6208 | 13.3317 | 13.7147 | 13.9411 | 14.3022 | 14.51 | 14.6439 | 14.8837 | 14.984 | 14.9771 | 14.9703 | 14.9637 | 14.957 | 14.9503 | 14.9437 | 15.0509 | 15.1596 | 15.1562 | 15.1552 | 15.244 | 15.3143 | 15.2791 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616
Mortlake OCGT | Low | 7.2259 | 8.0117 | 9.0016 | 9.2937 | 9.7193 | 10.479 | 11.0114 | 11.4136 | 11.7218 | 12.1223 | 12.6265 | 12.8306 | 12.8936 | 12.9529 | 13.0142 | 13.2832 | 13.6353 | 13.9443 | 14.2299 | 14.351 | 14.3595 | 14.4349 | 14.6178 | 14.7608 | 14.9346 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769
Newport | Low | 7.2259 | 8.0117 | 9.0016 | 9.2937 | 9.7193 | 10.479 | 11.0114 | 11.4136 | 11.7218 | 12.1223 | 12.6265 | 12.8306 | 12.8936 | 12.9529 | 13.0142 | 13.2832 | 13.6353 | 13.9443 | 14.2299 | 14.351 | 14.3595 | 14.4349 | 14.6178 | 14.7608 | 14.9346 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769
Oakey | Low | 7.9017 | 10.1707 | 11.9976 | 12.7001 | 13.2954 | 13.5795 | 13.5906 | 13.6599 | 13.7289 | 13.7298 | 13.7306 | 13.7314 | 13.7323 | 13.7498 | 13.7818 | 13.7971 | 13.9145 | 14.0312 | 14.0306 | 14.03 | 14.0294 | 14.0271 | 14.0231 | 14.0193 | 14.0155 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136
Quarantine | Low | 7.8112 | 8.5903 | 9.5736 | 9.8591 | 10.2782 | 11.0314 | 11.5573 | 11.953 | 12.3433 | 12.8259 | 13.3238 | 13.5215 | 13.5783 | 13.6315 | 13.6866 | 13.9494 | 14.2954 | 14.5984 | 14.9045 | 15.1013 | 15.1562 | 15.1552 | 15.244 | 15.3143 | 15.2791 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616
Roma | Low | 7.9017 | 10.1707 | 11.9976 | 12.7001 | 13.2954 | 13.5795 | 13.5906 | 13.6599 | 13.7289 | 13.7298 | 13.7306 | 13.7314 | 13.7323 | 13.7498 | 13.7818 | 13.7971 | 13.9145 | 14.0312 | 14.0306 | 14.03 | 14.0294 | 14.0271 | 14.0231 | 14.0193 | 14.0155 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136
Somerton | Low | 7.2259 | 8.0117 | 9.0016 | 9.2937 | 9.7193 | 10.479 | 11.0114 | 11.4136 | 11.7218 | 12.1223 | 12.6265 | 12.8306 | 12.8936 | 12.9529 | 13.0142 | 13.2832 | 13.6353 | 13.9443 | 14.2299 | 14.351 | 14.3595 | 14.4349 | 14.6178 | 14.7608 | 14.9346 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769
Tamar Valley OCGT | Low | 7.7089 | 8.4947 | 9.4846 | 9.7767 | 10.2023 | 10.9621 | 11.4944 | 11.8966 | 12.2048 | 12.6054 | 13.1096 | 13.3136 | 13.3766 | 13.436 | 13.4972 | 13.7662 | 14.1184 | 14.4273 | 14.7129 | 14.834 | 14.8425 | 14.9121 | 15.0833 | 15.215 | 15.3777 | 15.5146 | 15.5146 | 15.5146 | 15.5146 | 15.5146 | 15.5146
Torrens Island | Low | 7.8112 | 8.5903 | 9.5736 | 9.8591 | 10.2782 | 11.0314 | 11.5573 | 11.953 | 12.3433 | 12.8259 | 13.3238 | 13.5215 | 13.5783 | 13.6315 | 13.6866 | 13.9494 | 14.2954 | 14.5984 | 14.9045 | 15.1013 | 15.1562 | 15.1552 | 15.244 | 15.3143 | 15.2791 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616
Uranquinty | Low | 8.5261 | 9.3381 | 10.3244 | 11.0039 | 11.7165 | 12.1076 | 12.3459 | 12.719 | 13.0237 | 13.4209 | 13.9217 | 14.1224 | 14.182 | 14.2379 | 14.2959 | 14.5615 | 14.9104 | 15.216 | 15.4983 | 15.6161 | 15.6214 | 15.6684 | 15.7039 | 15.6858 | 15.6678 | 15.6588 | 15.6588 | 15.6588 | 15.6588 | 15.6588 | 15.6588
Valley Power | Low | 6.8043 | 7.5901 | 8.58 | 8.8721 | 9.2977 | 10.0575 | 10.5899 | 10.992 | 11.3003 | 11.7008 | 12.205 | 12.4091 | 12.4721 | 12.5314 | 12.5927 | 12.8616 | 13.2138 | 13.5228 | 13.8083 | 13.9294 | 13.938 | 14.0185 | 14.2116 | 14.3645 | 14.548 | 14.6951 | 14.6951 | 14.6951 | 14.6951 | 14.6951 | 14.6951
Liquid Fuel | High | 37.1803 | 35.1604 | 34.62 | 37.0668 | 37.7052 | 37.3252 | 36.8119 | 36.2052 | 35.604 | 35.0656 | 34.5771 | 34.1263 | 33.7314 | 33.3798 | 33.027 | 32.6874 | 32.3783 | 32.1047 | 31.863 | 31.6461 | 31.449 | 31.2675 | 31.0996 | 30.9437 | 30.7969 | 30.6579 | 30.2763 | 29.9004 | 29.5302 | 29.1654 | 28.8061
Liquid Fuel | Medium | 37.543 | 35.8708 | 34.7746 | 35.1044 | 35.3182 | 35.0145 | 34.5644 | 34.0309 | 33.4955 | 33.0053 | 32.5528 | 32.1326 | 31.7645 | 31.4368 | 31.1066 | 30.7857 | 30.4894 | 30.2211 | 29.9766 | 29.7488 | 29.5326 | 29.3245 | 29.123 | 28.927 | 28.7344 | 28.5453 | 28.1835 | 27.8273 | 27.4766 | 27.1311 | 26.7909
Liquid Fuel | Low | 37.954 | 36.5702 | 34.8107 | 33.0439 | 32.8209 | 32.543 | 32.1209 | 31.6319 | 31.1412 | 30.6849 | 30.2582 | 29.8605 | 29.5118 | 29.2013 | 28.8884 | 28.5828 | 28.2971 | 28.0337 | 27.7878 | 27.5523 | 27.3224 | 27.0948 | 26.8685 | 26.643 | 26.4169 | 26.191 | 25.8517 | 25.5177 | 25.1889 | 24.8653 | 24.5467

## New Entant Fuel Costs
Fuel Costs for New Entrants (2014-15 $/GJ)
Year Ending June
Profile | Scenario | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Black Coal - NQ | High | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223
Black Coal - NQ | Medium | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223
Black Coal - NQ | Low | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223 | 1.9223
Black Coal - CQ | High | 2.3789 | 2.1753 | 2.1528 | 2.4958 | 2.6036 | 2.5877 | 2.5673 | 2.536 | 2.4979 | 2.4614 | 2.4263 | 2.3931 | 2.3677 | 2.3527 | 2.3381 | 2.3225 | 2.3074 | 2.2936 | 2.2818 | 2.2716 | 2.2631 | 2.2558 | 2.2494 | 2.2439 | 2.2387 | 2.234 | 2.2281 | 2.223 | 2.2178 | 2.2125 | 2.2071
Black Coal - CQ | Medium | 2.4237 | 2.2601 | 2.1583 | 2.2218 | 2.2691 | 2.2595 | 2.2401 | 2.2113 | 2.1777 | 2.1457 | 2.1147 | 2.0851 | 2.0626 | 2.0497 | 2.0372 | 2.0236 | 2.0103 | 1.9981 | 1.9873 | 1.9779 | 1.9697 | 1.9625 | 1.9558 | 1.9498 | 1.9439 | 1.9384 | 1.9321 | 1.9263 | 1.9205 | 1.9146 | 1.9086
Black Coal - CQ | Low | 2.4744 | 2.3475 | 2.1567 | 1.9512 | 1.942 | 1.9358 | 1.9166 | 1.8894 | 1.8593 | 1.831 | 1.8033 | 1.7769 | 1.7568 | 1.7456 | 1.7347 | 1.7229 | 1.7113 | 1.7005 | 1.6909 | 1.6824 | 1.6748 | 1.6678 | 1.6613 | 1.6551 | 1.649 | 1.6432 | 1.6368 | 1.6309 | 1.6248 | 1.6187 | 1.6126
Black Coal - SWQ | High | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375
Black Coal - SWQ | Medium | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375
Black Coal - SWQ | Low | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 1.5224 | 1.5124 | 1.5027 | 1.4923 | 1.4819 | 1.4723 | 1.4638 | 1.4562 | 1.4495 | 1.4433 | 1.4375 | 1.432 | 1.4266 | 1.4214 | 1.4158 | 1.4104 | 1.405 | 1.3996 | 1.3942
Black Coal - NNS | High | 2.7436 | 2.5302 | 2.5065 | 2.8661 | 2.9791 | 2.9624 | 2.9411 | 2.9083 | 2.8683 | 2.83 | 2.7933 | 2.7584 | 2.7318 | 2.7161 | 2.7008 | 2.6844 | 2.6686 | 2.6542 | 2.6417 | 2.6311 | 2.6221 | 2.6145 | 2.6079 | 2.602 | 2.5966 | 2.5916 | 2.5855 | 2.5802 | 2.5747 | 2.5691 | 2.5635
Black Coal - NNS | Medium | 2.7613 | 2.592 | 2.4865 | 2.5522 | 2.6012 | 2.5913 | 2.5712 | 2.5414 | 2.5066 | 2.4735 | 2.4414 | 2.4107 | 2.3874 | 2.3741 | 2.361 | 2.347 | 2.3332 | 2.3206 | 2.3095 | 2.2997 | 2.2912 | 2.2837 | 2.2768 | 2.2705 | 2.2645 | 2.2588 | 2.2522 | 2.2463 | 2.2402 | 2.2341 | 2.2279
Black Coal - NNS | Low | 2.8138 | 2.6824 | 2.4848 | 2.272 | 2.2625 | 2.2561 | 2.2362 | 2.2081 | 2.1768 | 2.1475 | 2.1189 | 2.0915 | 2.0707 | 2.0591 | 2.0478 | 2.0356 | 2.0236 | 2.0124 | 2.0025 | 1.9937 | 1.9858 | 1.9785 | 1.9718 | 1.9654 | 1.9591 | 1.953 | 1.9465 | 1.9403 | 1.934 | 1.9277 | 1.9213
Black Coal - NCEN | High | 2.7958 | 2.5829 | 2.5593 | 2.9179 | 3.0307 | 3.014 | 2.9927 | 2.96 | 2.9201 | 2.882 | 2.8453 | 2.8106 | 2.784 | 2.7684 | 2.7531 | 2.7367 | 2.721 | 2.7066 | 2.6942 | 2.6836 | 2.6746 | 2.667 | 2.6604 | 2.6546 | 2.6492 | 2.6442 | 2.6381 | 2.6328 | 2.6274 | 2.6218 | 2.6162
Black Coal - NCEN | Medium | 2.8282 | 2.6572 | 2.5506 | 2.617 | 2.6665 | 2.6565 | 2.6362 | 2.6061 | 2.5709 | 2.5375 | 2.505 | 2.4741 | 2.4505 | 2.4371 | 2.4239 | 2.4097 | 2.3958 | 2.383 | 2.3718 | 2.362 | 2.3534 | 2.3458 | 2.3388 | 2.3325 | 2.3264 | 2.3206 | 2.314 | 2.308 | 2.3019 | 2.2957 | 2.2894
Black Coal - NCEN | Low | 2.8812 | 2.7486 | 2.5489 | 2.334 | 2.3244 | 2.3179 | 2.2978 | 2.2694 | 2.2378 | 2.2082 | 2.1793 | 2.1516 | 2.1306 | 2.1189 | 2.1075 | 2.0952 | 2.083 | 2.0718 | 2.0617 | 2.0528 | 2.0448 | 2.0375 | 2.0307 | 2.0242 | 2.0179 | 2.0118 | 2.0051 | 1.9989 | 1.9925 | 1.9862 | 1.9798
Black Coal - SWNSW | High | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188
Black Coal - SWNSW | Medium | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188
Black Coal - SWNSW | Low | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188 | 1.3188
Brown Coal - LV | High | 0.39578 | 0.39974 | 0.40373 | 0.40777 | 0.41185 | 0.41597 | 0.42013 | 0.42433 | 0.42857 | 0.43286 | 0.43719 | 0.44156 | 0.44597 | 0.45043 | 0.45494 | 0.45949 | 0.46408 | 0.46872 | 0.47341 | 0.47814 | 0.48293 | 0.48776 | 0.49263 | 0.49756 | 0.50253 | 0.50756 | 0.51246 | 0.51745 | 0.52242 | 0.52739 | 0.53234
Brown Coal - LV | Medium | 0.39578 | 0.39974 | 0.40373 | 0.40777 | 0.41185 | 0.41597 | 0.42013 | 0.42433 | 0.42857 | 0.43286 | 0.43719 | 0.44156 | 0.44597 | 0.45043 | 0.45494 | 0.45949 | 0.46408 | 0.46872 | 0.47341 | 0.47814 | 0.48293 | 0.48776 | 0.49263 | 0.49756 | 0.50253 | 0.50756 | 0.51246 | 0.51745 | 0.52242 | 0.52739 | 0.53234
Brown Coal - LV | Low | 0.39578 | 0.39974 | 0.40373 | 0.40777 | 0.41185 | 0.41597 | 0.42013 | 0.42433 | 0.42857 | 0.43286 | 0.43719 | 0.44156 | 0.44597 | 0.45043 | 0.45494 | 0.45949 | 0.46408 | 0.46872 | 0.47341 | 0.47814 | 0.48293 | 0.48776 | 0.49263 | 0.49756 | 0.50253 | 0.50756 | 0.51246 | 0.51745 | 0.52242 | 0.52739 | 0.53234
CCGT - Without CCS (ADE) | Medium | 4.9074 | 5.6332 | 6.4668 | 6.6271 | 6.6913 | 7.075 | 7.5103 | 7.7928 | 7.8622 | 7.9206 | 8.1186 | 8.3009 | 8.4869 | 8.7275 | 8.9968 | 9.2007 | 9.2274 | 9.2354 | 9.2893 | 9.5827 | 9.825 | 9.855 | 9.996 | 10.1196 | 10.1614 | 10.1966 | 10.1966 | 10.1966 | 10.1966 | 10.1966 | 10.1966
CCGT - Without CCS (CAN) | Medium | 5.4533 | 6.503 | 6.9535 | 6.7888 | 6.7465 | 7.1291 | 7.564 | 7.8464 | 7.9153 | 7.9727 | 8.1472 | 8.3286 | 8.448 | 8.5996 | 8.8683 | 9.0713 | 9.0975 | 9.1051 | 9.1584 | 9.4511 | 9.6929 | 9.7243 | 9.8685 | 10.0657 | 10.1794 | 10.2145 | 10.2145 | 10.2145 | 10.2145 | 10.2145 | 10.2145
CCGT - Without CCS (CQ) | Medium | 5.2282 | 7.136 | 8.1957 | 7.9212 | 7.9266 | 8.2478 | 8.6042 | 8.7446 | 8.7762 | 8.7835 | 8.8918 | 8.993 | 8.9886 | 8.9842 | 9.0183 | 9.0561 | 9.2556 | 9.4549 | 9.4579 | 9.4608 | 9.462 | 9.4565 | 9.4888 | 9.54 | 9.5959 | 9.6382 | 9.6382 | 9.6382 | 9.6382 | 9.6382 | 9.6382
CCGT - Without CCS (CVIC) | Medium | 4.5099 | 5.2405 | 6.079 | 6.2442 | 6.3132 | 6.7016 | 7.1417 | 7.4289 | 7.503 | 7.566 | 7.7687 | 7.9555 | 8.1461 | 8.3912 | 8.6649 | 8.8734 | 8.9045 | 8.9169 | 8.9751 | 9.2729 | 9.5196 | 9.5554 | 9.7037 | 9.8343 | 9.8831 | 9.9218 | 9.9218 | 9.9218 | 9.9218 | 9.9218 | 9.9218
CCGT - Without CCS (LV) | Medium | 3.9005 | 4.633 | 5.4733 | 5.6402 | 5.7109 | 6.1011 | 6.5429 | 6.8319 | 6.9077 | 6.9724 | 7.1545 | 7.343 | 7.4691 | 7.6274 | 7.9028 | 8.113 | 8.1458 | 8.1598 | 8.2197 | 8.519 | 8.7673 | 8.8131 | 8.9796 | 9.1984 | 9.3333 | 9.3788 | 9.3788 | 9.3788 | 9.3788 | 9.3788 | 9.3788
CCGT - Without CCS (MEL) | Medium | 4.3221 | 5.0545 | 5.8948 | 6.0617 | 6.1324 | 6.5226 | 6.9644 | 7.2534 | 7.3292 | 7.3939 | 7.576 | 7.7645 | 7.8906 | 8.0489 | 8.3244 | 8.5345 | 8.5673 | 8.5813 | 8.6412 | 8.9405 | 9.1889 | 9.2295 | 9.3858 | 9.5947 | 9.7199 | 9.7607 | 9.7607 | 9.7607 | 9.7607 | 9.7607 | 9.7607
CCGT - Without CCS (NCEN) | Medium | 5.8444 | 6.892 | 7.3401 | 7.1729 | 7.128 | 7.5085 | 7.941 | 8.2209 | 8.2877 | 8.3429 | 8.5151 | 8.6944 | 8.8115 | 8.9607 | 9.2273 | 9.4282 | 9.4521 | 9.4578 | 9.5088 | 9.7992 | 10.039 | 10.0653 | 10.2012 | 10.3903 | 10.496 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271
CCGT - Without CCS (NNS) | Medium | 4.511 | 4.7072 | 5.9755 | 7.023 | 6.9782 | 7.2941 | 7.5428 | 7.6783 | 7.7052 | 7.708 | 7.8426 | 8.0219 | 8.139 | 8.2883 | 8.5549 | 8.7558 | 8.7797 | 8.7853 | 8.8364 | 9.1268 | 9.3665 | 9.3928 | 9.5317 | 9.7268 | 9.8387 | 9.8729 | 9.8729 | 9.8729 | 9.8729 | 9.8729 | 9.8729
CCGT - Without CCS (NQ) | Medium | 5.9218 | 5.9175 | 5.9133 | 6.2452 | 6.5773 | 6.941 | 7.3048 | 7.3006 | 7.2964 | 7.2923 | 7.2882 | 7.2841 | 7.2801 | 7.276 | 7.272 | 7.268 | 7.264 | 7.2601 | 7.2561 | 7.2522 | 7.2483 | 7.2366 | 7.2175 | 7.1989 | 7.1806 | 7.1716 | 7.1716 | 7.1716 | 7.1716 | 7.1716 | 7.1716
CCGT - Without CCS (NSA) | Medium | 5.4951 | 6.7667 | 7.3863 | 7.3127 | 7.3124 | 8.1844 | 9.2033 | 9.4722 | 9.5177 | 9.5135 | 9.6106 | 9.7008 | 9.6856 | 9.6707 | 9.6944 | 9.7221 | 9.9116 | 10.1011 | 10.0945 | 10.088 | 10.0816 | 10.0655 | 10.0828 | 10.1196 | 10.1614 | 10.1966 | 10.1966 | 10.1966 | 10.1966 | 10.1966 | 10.1966
CCGT - Without CCS (NVIC) | Medium | 4.9215 | 5.654 | 6.4943 | 6.6612 | 6.7319 | 7.1221 | 7.5639 | 7.8529 | 7.9287 | 7.9934 | 8.1755 | 8.364 | 8.4901 | 8.6484 | 8.9238 | 9.134 | 9.1668 | 9.1808 | 9.2407 | 9.54 | 9.7883 | 9.8217 | 9.9635 | 10.1584 | 10.2698 | 10.3038 | 10.3038 | 10.3038 | 10.3038 | 10.3038 | 10.3038
CCGT - Without CCS (SEQ) | Medium | 4.8033 | 6.6314 | 7.9647 | 7.8908 | 7.8902 | 8.2055 | 8.5563 | 8.6912 | 8.7175 | 8.7196 | 8.8231 | 8.9195 | 8.9106 | 8.9018 | 8.9316 | 8.9654 | 9.1609 | 9.3565 | 9.3558 | 9.3551 | 9.3546 | 9.3502 | 9.385 | 9.5734 | 9.7631 | 9.8032 | 9.8032 | 9.8032 | 9.8032 | 9.8032 | 9.8032
CCGT - Without CCS (SESA) | Medium | 5.0854 | 5.8103 | 6.6431 | 6.8025 | 6.8659 | 7.2487 | 7.6832 | 7.9649 | 8.0334 | 8.0909 | 8.2881 | 8.4695 | 8.6547 | 8.8945 | 9.163 | 9.3662 | 9.392 | 9.3992 | 9.4523 | 9.7449 | 9.9865 | 10.0141 | 10.1513 | 10.271 | 10.3091 | 10.3426 | 10.3426 | 10.3426 | 10.3426 | 10.3426 | 10.3426
CCGT - Without CCS (SWNSW) | Medium | 5.6223 | 6.3809 | 7.2177 | 7.381 | 7.4482 | 7.8349 | 8.2733 | 8.5588 | 8.6312 | 8.6925 | 8.8712 | 9.0563 | 9.179 | 9.3339 | 9.6061 | 9.8128 | 9.8423 | 9.853 | 9.9096 | 10.2057 | 10.4508 | 10.4744 | 10.5737 | 10.6565 | 10.6852 | 10.714 | 10.714 | 10.714 | 10.714 | 10.714 | 10.714
CCGT - Without CCS (SWQ) | Medium | 4.5178 | 6.144 | 7.4076 | 7.3387 | 7.3396 | 7.7255 | 8.0096 | 8.146 | 8.2418 | 8.2455 | 8.3504 | 8.4482 | 8.4407 | 8.4335 | 8.4647 | 8.4999 | 8.6968 | 8.8938 | 8.8946 | 8.8953 | 8.8962 | 8.8981 | 8.944 | 9.1432 | 9.3433 | 9.3886 | 9.3886 | 9.3886 | 9.3886 | 9.3886 | 9.3886
CCGT - Without CCS (TAS) | Medium | 4.8051 | 5.5376 | 6.3778 | 6.5447 | 6.6155 | 7.0056 | 7.4475 | 7.7364 | 7.8122 | 7.877 | 8.0591 | 8.2476 | 8.3737 | 8.532 | 8.8074 | 9.0175 | 9.0503 | 9.0643 | 9.1242 | 9.4236 | 9.6719 | 9.7066 | 9.8513 | 10.0489 | 10.163 | 10.1983 | 10.1983 | 10.1983 | 10.1983 | 10.1983 | 10.1983
OCGT - Without CCS (ADE) | Medium | 6.9074 | 7.6332 | 8.4668 | 8.6271 | 8.6913 | 9.075 | 9.5103 | 9.7928 | 9.8622 | 9.9206 | 10.1186 | 10.3009 | 10.4869 | 10.7275 | 10.9968 | 11.2007 | 11.2274 | 11.2354 | 11.2893 | 11.5827 | 11.825 | 11.855 | 11.996 | 12.1196 | 12.1614 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966
OCGT - Without CCS (CAN) | Medium | 7.4533 | 8.503 | 8.9535 | 8.7888 | 8.7465 | 9.1291 | 9.564 | 9.8464 | 9.9153 | 9.9727 | 10.1472 | 10.3286 | 10.448 | 10.5996 | 10.8683 | 11.0713 | 11.0975 | 11.1051 | 11.1584 | 11.4511 | 11.6929 | 11.7243 | 11.8685 | 12.0657 | 12.1794 | 12.2145 | 12.2145 | 12.2145 | 12.2145 | 12.2145 | 12.2145
OCGT - Without CCS (CQ) | Medium | 7.2282 | 9.136 | 10.1957 | 9.9212 | 9.9266 | 10.2478 | 10.6042 | 10.7446 | 10.7762 | 10.7835 | 10.8918 | 10.993 | 10.9886 | 10.9842 | 11.0183 | 11.0561 | 11.2556 | 11.4549 | 11.4579 | 11.4608 | 11.462 | 11.4565 | 11.4888 | 11.54 | 11.5959 | 11.6382 | 11.6382 | 11.6382 | 11.6382 | 11.6382 | 11.6382
OCGT - Without CCS (CVIC) | Medium | 6.5099 | 7.2405 | 8.079 | 8.2442 | 8.3132 | 8.7016 | 9.1417 | 9.4289 | 9.503 | 9.566 | 9.7687 | 9.9555 | 10.1461 | 10.3912 | 10.6649 | 10.8734 | 10.9045 | 10.9169 | 10.9751 | 11.2729 | 11.5196 | 11.5554 | 11.7037 | 11.8343 | 11.8831 | 11.9218 | 11.9218 | 11.9218 | 11.9218 | 11.9218 | 11.9218
OCGT - Without CCS (LV) | Medium | 5.9005 | 6.633 | 7.4733 | 7.6402 | 7.7109 | 8.1011 | 8.5429 | 8.8319 | 8.9077 | 8.9724 | 9.1545 | 9.343 | 9.4691 | 9.6274 | 9.9028 | 10.113 | 10.1458 | 10.1598 | 10.2197 | 10.519 | 10.7673 | 10.8131 | 10.9796 | 11.1984 | 11.3333 | 11.3788 | 11.3788 | 11.3788 | 11.3788 | 11.3788 | 11.3788
OCGT - Without CCS (MEL) | Medium | 6.3221 | 7.0545 | 7.8948 | 8.0617 | 8.1324 | 8.5226 | 8.9644 | 9.2534 | 9.3292 | 9.3939 | 9.576 | 9.7645 | 9.8906 | 10.0489 | 10.3244 | 10.5345 | 10.5673 | 10.5813 | 10.6412 | 10.9405 | 11.1889 | 11.2295 | 11.3858 | 11.5947 | 11.7199 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607 | 11.7607
OCGT - Without CCS (NCEN) | Medium | 7.8444 | 8.892 | 9.3401 | 9.1729 | 9.128 | 9.5085 | 9.941 | 10.2209 | 10.2877 | 10.3429 | 10.5151 | 10.6944 | 10.8115 | 10.9607 | 11.2273 | 11.4282 | 11.4521 | 11.4578 | 11.5088 | 11.7992 | 12.039 | 12.0653 | 12.2012 | 12.3903 | 12.496 | 12.5271 | 12.5271 | 12.5271 | 12.5271 | 12.5271 | 12.5271
OCGT - Without CCS (NNS) | Medium | 6.511 | 6.7072 | 7.9755 | 9.023 | 8.9782 | 9.2941 | 9.5428 | 9.6783 | 9.7052 | 9.708 | 9.8426 | 10.0219 | 10.139 | 10.2883 | 10.5549 | 10.7558 | 10.7797 | 10.7853 | 10.8364 | 11.1268 | 11.3665 | 11.3928 | 11.5317 | 11.7268 | 11.8387 | 11.8729 | 11.8729 | 11.8729 | 11.8729 | 11.8729 | 11.8729
OCGT - Without CCS (NQ) | Medium | 7.9218 | 7.9175 | 7.9133 | 8.2452 | 8.5773 | 8.941 | 9.3048 | 9.3006 | 9.2964 | 9.2923 | 9.2882 | 9.2841 | 9.2801 | 9.276 | 9.272 | 9.268 | 9.264 | 9.2601 | 9.2561 | 9.2522 | 9.2483 | 9.2366 | 9.2175 | 9.1989 | 9.1806 | 9.1716 | 9.1716 | 9.1716 | 9.1716 | 9.1716 | 9.1716
OCGT - Without CCS (NSA) | Medium | 7.4951 | 8.7667 | 9.3863 | 9.3127 | 9.3124 | 10.1844 | 11.2033 | 11.4722 | 11.5177 | 11.5135 | 11.6106 | 11.7008 | 11.6856 | 11.6707 | 11.6944 | 11.7221 | 11.9116 | 12.1011 | 12.0945 | 12.088 | 12.0816 | 12.0655 | 12.0828 | 12.1196 | 12.1614 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966 | 12.1966
OCGT - Without CCS (NVIC) | Medium | 6.9215 | 7.654 | 8.4943 | 8.6612 | 8.7319 | 9.1221 | 9.5639 | 9.8529 | 9.9287 | 9.9934 | 10.1755 | 10.364 | 10.4901 | 10.6484 | 10.9238 | 11.134 | 11.1668 | 11.1808 | 11.2407 | 11.54 | 11.7883 | 11.8217 | 11.9635 | 12.1584 | 12.2698 | 12.3038 | 12.3038 | 12.3038 | 12.3038 | 12.3038 | 12.3038
OCGT - Without CCS (SEQ) | Medium | 6.8033 | 8.6314 | 9.9647 | 9.8908 | 9.8902 | 10.2055 | 10.5563 | 10.6912 | 10.7175 | 10.7196 | 10.8231 | 10.9195 | 10.9106 | 10.9018 | 10.9316 | 10.9654 | 11.1609 | 11.3565 | 11.3558 | 11.3551 | 11.3546 | 11.3502 | 11.385 | 11.5734 | 11.7631 | 11.8032 | 11.8032 | 11.8032 | 11.8032 | 11.8032 | 11.8032
OCGT - Without CCS (SESA) | Medium | 7.0854 | 7.8103 | 8.6431 | 8.8025 | 8.8659 | 9.2487 | 9.6832 | 9.9649 | 10.0334 | 10.0909 | 10.2881 | 10.4695 | 10.6547 | 10.8945 | 11.163 | 11.3662 | 11.392 | 11.3992 | 11.4523 | 11.7449 | 11.9865 | 12.0141 | 12.1513 | 12.271 | 12.3091 | 12.3426 | 12.3426 | 12.3426 | 12.3426 | 12.3426 | 12.3426
OCGT - Without CCS (SWNSW) | Medium | 7.6223 | 8.3809 | 9.2177 | 9.381 | 9.4482 | 9.8349 | 10.2733 | 10.5588 | 10.6312 | 10.6925 | 10.8712 | 11.0563 | 11.179 | 11.3339 | 11.6061 | 11.8128 | 11.8423 | 11.853 | 11.9096 | 12.2057 | 12.4508 | 12.4744 | 12.5737 | 12.6565 | 12.6852 | 12.714 | 12.714 | 12.714 | 12.714 | 12.714 | 12.714
OCGT - Without CCS (SWQ) | Medium | 6.5178 | 8.144 | 9.4076 | 9.3387 | 9.3396 | 9.7255 | 10.0096 | 10.146 | 10.2418 | 10.2455 | 10.3504 | 10.4482 | 10.4407 | 10.4335 | 10.4647 | 10.4999 | 10.6968 | 10.8938 | 10.8946 | 10.8953 | 10.8962 | 10.8981 | 10.944 | 11.1432 | 11.3433 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886 | 11.3886
OCGT - Without CCS (TAS) | Medium | 6.8051 | 7.5376 | 8.3778 | 8.5447 | 8.6155 | 9.0056 | 9.4475 | 9.7364 | 9.8122 | 9.877 | 10.0591 | 10.2476 | 10.3737 | 10.532 | 10.8074 | 11.0175 | 11.0503 | 11.0643 | 11.1242 | 11.4236 | 11.6719 | 11.7066 | 11.8513 | 12.0489 | 12.163 | 12.1983 | 12.1983 | 12.1983 | 12.1983 | 12.1983 | 12.1983
CCGT - Without CCS (ADE) | High | 4.5155 | 5.3527 | 6.1915 | 5.991 | 5.9878 | 6.4522 | 6.9977 | 7.2715 | 7.2651 | 7.2587 | 7.3957 | 7.6219 | 7.7525 | 7.7962 | 7.8143 | 7.8341 | 7.9509 | 8.1492 | 8.2285 | 8.2225 | 8.2165 | 8.2651 | 8.4284 | 8.5363 | 8.5819 | 8.6314 | 8.6314 | 8.6314 | 8.6314 | 8.6314 | 8.6314
CCGT - Without CCS (CAN) | High | 4.7705 | 5.666 | 6.374 | 6.1141 | 6.043 | 6.5063 | 7.0514 | 7.325 | 7.3181 | 7.3109 | 7.4466 | 7.6719 | 7.802 | 7.8451 | 7.8627 | 7.8816 | 7.9093 | 8.0246 | 8.1693 | 8.2232 | 8.2168 | 8.2006 | 8.3009 | 8.4118 | 8.4713 | 8.5333 | 8.5333 | 8.5333 | 8.5333 | 8.5333 | 8.5333
CCGT - Without CCS (CQ) | High | 4.2926 | 6.2467 | 7.5641 | 6.9185 | 6.4757 | 6.5976 | 7.0414 | 7.3106 | 7.132 | 7.011 | 7.0153 | 7.1046 | 7.2719 | 7.373 | 7.3966 | 7.4102 | 7.5649 | 7.7429 | 7.8114 | 7.8453 | 7.8453 | 7.8453 | 7.9425 | 8.0346 | 8.0512 | 8.073 | 8.073 | 8.073 | 8.073 | 8.073 | 8.073
CCGT - Without CCS (CVIC) | High | 4.118 | 4.96 | 5.8037 | 5.608 | 5.6097 | 6.0788 | 6.6291 | 6.9076 | 6.9058 | 6.9041 | 7.0458 | 7.2765 | 7.4117 | 7.4598 | 7.4825 | 7.5067 | 7.628 | 7.8307 | 7.9143 | 7.9126 | 7.9111 | 7.9655 | 8.1361 | 8.251 | 8.3036 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566
CCGT - Without CCS (LV) | High | 3.5086 | 4.3525 | 5.198 | 5.004 | 5.0074 | 5.4783 | 6.0303 | 6.3105 | 6.3105 | 6.3105 | 6.4539 | 6.6863 | 6.8231 | 6.873 | 6.8973 | 6.9232 | 6.9577 | 7.0793 | 7.2307 | 7.2912 | 7.2912 | 7.2894 | 7.412 | 7.5446 | 7.6253 | 7.6977 | 7.6977 | 7.6977 | 7.6977 | 7.6977 | 7.6977
CCGT - Without CCS (MEL) | High | 3.9302 | 4.774 | 5.6195 | 5.4255 | 5.4289 | 5.8998 | 6.4519 | 6.732 | 6.732 | 6.732 | 6.8754 | 7.1078 | 7.2446 | 7.2945 | 7.3188 | 7.3448 | 7.3792 | 7.5008 | 7.6522 | 7.7127 | 7.7127 | 7.7058 | 7.8182 | 7.9409 | 8.0119 | 8.0795 | 8.0795 | 8.0795 | 8.0795 | 8.0795 | 8.0795
CCGT - Without CCS (NCEN) | High | 5.1616 | 6.0549 | 6.7606 | 6.4983 | 6.4246 | 6.8857 | 7.4284 | 7.6996 | 7.6906 | 7.681 | 7.8144 | 8.0376 | 8.1655 | 8.2063 | 8.2218 | 8.2385 | 8.264 | 8.3773 | 8.5198 | 8.5714 | 8.5629 | 8.5416 | 8.6336 | 8.7364 | 8.7879 | 8.846 | 8.846 | 8.846 | 8.846 | 8.846 | 8.846
CCGT - Without CCS (NNS) | High | 3.6761 | 3.7657 | 5.191 | 6.3484 | 6.2747 | 6.7358 | 7.0173 | 7.0271 | 7.0181 | 7.0086 | 7.142 | 7.3652 | 7.4931 | 7.5338 | 7.5494 | 7.5661 | 7.5916 | 7.7048 | 7.8474 | 7.8989 | 7.8904 | 7.8691 | 7.9641 | 8.0729 | 8.1306 | 8.1918 | 8.1918 | 8.1918 | 8.1918 | 8.1918 | 8.1918
CCGT - Without CCS (NQ) | High | 4.9131 | 4.9088 | 4.9046 | 4.9003 | 4.8961 | 4.8919 | 4.8877 | 4.8836 | 4.8794 | 4.9911 | 5.1028 | 5.4349 | 6.3274 | 6.9025 | 6.9171 | 6.9222 | 7.0684 | 7.2381 | 7.2986 | 7.3245 | 7.3182 | 7.3088 | 7.392 | 7.4985 | 7.5056 | 7.4966 | 7.4966 | 7.4966 | 7.4966 | 7.4966 | 7.4966
CCGT - Without CCS (NSA) | High | 4.8122 | 5.8775 | 6.7547 | 6.31 | 6.0544 | 6.6799 | 7.6187 | 8.0637 | 7.8735 | 7.7411 | 7.7341 | 7.8124 | 7.9688 | 8.0595 | 8.0727 | 8.0762 | 8.2209 | 8.3891 | 8.448 | 8.4725 | 8.4648 | 8.4543 | 8.5366 | 8.6141 | 8.6167 | 8.6314 | 8.6314 | 8.6314 | 8.6314 | 8.6314 | 8.6314
CCGT - Without CCS (NVIC) | High | 4.5296 | 5.3735 | 6.219 | 6.025 | 6.0284 | 6.4993 | 7.0513 | 7.3315 | 7.3315 | 7.3315 | 7.4749 | 7.7073 | 7.8441 | 7.894 | 7.9183 | 7.9443 | 7.9787 | 8.1003 | 8.2517 | 8.3122 | 8.3122 | 8.298 | 8.3959 | 8.5045 | 8.5618 | 8.6226 | 8.6226 | 8.6226 | 8.6226 | 8.6226 | 8.6226
CCGT - Without CCS (SEQ) | High | 3.8676 | 5.7422 | 7.333 | 6.8881 | 6.4392 | 6.5553 | 6.9934 | 7.2572 | 7.0733 | 6.9472 | 6.9466 | 7.0311 | 7.3445 | 7.5913 | 7.6091 | 7.6172 | 7.7664 | 7.9393 | 8.0027 | 8.0316 | 8.0284 | 8.0253 | 8.1181 | 8.2059 | 8.2184 | 8.2381 | 8.2381 | 8.2381 | 8.2381 | 8.2381 | 8.2381
CCGT - Without CCS (SESA) | High | 4.6935 | 5.5298 | 6.3678 | 6.1664 | 6.1624 | 6.6259 | 7.1706 | 7.4435 | 7.4363 | 7.4291 | 7.5652 | 7.7905 | 7.9203 | 7.9632 | 7.9806 | 7.9995 | 8.1154 | 8.313 | 8.3915 | 8.3847 | 8.378 | 8.4242 | 8.5837 | 8.6877 | 8.7296 | 8.7774 | 8.7774 | 8.7774 | 8.7774 | 8.7774 | 8.7774
CCGT - Without CCS (SWNSW) | High | 5.2304 | 6.1004 | 6.9424 | 6.6987 | 6.6486 | 7.1621 | 7.7607 | 8.0374 | 8.034 | 8.0306 | 8.1705 | 8.3894 | 8.5228 | 8.5795 | 8.6005 | 8.6231 | 8.6542 | 8.7725 | 8.9206 | 8.9779 | 8.9746 | 8.9507 | 9.0327 | 9.1258 | 9.1316 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488
CCGT - Without CCS (SWQ) | High | 3.5821 | 5.2548 | 6.7065 | 6.2666 | 5.8886 | 6.0753 | 6.4468 | 6.712 | 6.5977 | 6.473 | 6.4739 | 6.5599 | 6.8747 | 7.1229 | 7.1422 | 7.1517 | 7.3024 | 7.4766 | 7.5415 | 7.5718 | 7.57 | 7.5732 | 7.6771 | 7.8038 | 7.8307 | 7.8314 | 7.8314 | 7.8314 | 7.8314 | 7.8314 | 7.8314
CCGT - Without CCS (TAS) | High | 4.4132 | 5.2571 | 6.1025 | 5.9086 | 5.912 | 6.3828 | 6.9349 | 7.2151 | 7.2151 | 7.2151 | 7.3584 | 7.5908 | 7.7277 | 7.7775 | 7.8019 | 7.8278 | 7.8622 | 7.9838 | 8.1352 | 8.1958 | 8.1958 | 8.1829 | 8.2837 | 8.395 | 8.455 | 8.5172 | 8.5172 | 8.5172 | 8.5172 | 8.5172 | 8.5172
OCGT - Without CCS (ADE) | High | 6.5155 | 7.3527 | 8.1915 | 7.991 | 7.9878 | 8.4522 | 8.9977 | 9.2715 | 9.2651 | 9.2587 | 9.3957 | 9.6219 | 9.7525 | 9.7962 | 9.8143 | 9.8341 | 9.9509 | 10.1492 | 10.2285 | 10.2225 | 10.2165 | 10.2651 | 10.4284 | 10.5363 | 10.5819 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314
OCGT - Without CCS (CAN) | High | 6.7705 | 7.666 | 8.374 | 8.1141 | 8.043 | 8.5063 | 9.0514 | 9.325 | 9.3181 | 9.3109 | 9.4466 | 9.6719 | 9.802 | 9.8451 | 9.8627 | 9.8816 | 9.9093 | 10.0246 | 10.1693 | 10.2232 | 10.2168 | 10.2006 | 10.3009 | 10.4118 | 10.4713 | 10.5333 | 10.5333 | 10.5333 | 10.5333 | 10.5333 | 10.5333
OCGT - Without CCS (CQ) | High | 6.2926 | 8.2467 | 9.5641 | 8.9185 | 8.4757 | 8.5976 | 9.0414 | 9.3106 | 9.132 | 9.011 | 9.0153 | 9.1046 | 9.2719 | 9.373 | 9.3966 | 9.4102 | 9.5649 | 9.7429 | 9.8114 | 9.8453 | 9.8453 | 9.8453 | 9.9425 | 10.0346 | 10.0512 | 10.073 | 10.073 | 10.073 | 10.073 | 10.073 | 10.073
OCGT - Without CCS (CVIC) | High | 6.118 | 6.96 | 7.8037 | 7.608 | 7.6097 | 8.0788 | 8.6291 | 8.9076 | 8.9058 | 8.9041 | 9.0458 | 9.2765 | 9.4117 | 9.4598 | 9.4825 | 9.5067 | 9.628 | 9.8307 | 9.9143 | 9.9126 | 9.9111 | 9.9655 | 10.1361 | 10.251 | 10.3036 | 10.3566 | 10.3566 | 10.3566 | 10.3566 | 10.3566 | 10.3566
OCGT - Without CCS (LV) | High | 5.5086 | 6.3525 | 7.198 | 7.004 | 7.0074 | 7.4783 | 8.0303 | 8.3105 | 8.3105 | 8.3105 | 8.4539 | 8.6863 | 8.8231 | 8.873 | 8.8973 | 8.9232 | 8.9577 | 9.0793 | 9.2307 | 9.2912 | 9.2912 | 9.2894 | 9.412 | 9.5446 | 9.6253 | 9.6977 | 9.6977 | 9.6977 | 9.6977 | 9.6977 | 9.6977
OCGT - Without CCS (MEL) | High | 5.9302 | 6.774 | 7.6195 | 7.4255 | 7.4289 | 7.8998 | 8.4519 | 8.732 | 8.732 | 8.732 | 8.8754 | 9.1078 | 9.2446 | 9.2945 | 9.3188 | 9.3448 | 9.3792 | 9.5008 | 9.6522 | 9.7127 | 9.7127 | 9.7058 | 9.8182 | 9.9409 | 10.0119 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795 | 10.0795
OCGT - Without CCS (NCEN) | High | 7.1616 | 8.0549 | 8.7606 | 8.4983 | 8.4246 | 8.8857 | 9.4284 | 9.6996 | 9.6906 | 9.681 | 9.8144 | 10.0376 | 10.1655 | 10.2063 | 10.2218 | 10.2385 | 10.264 | 10.3773 | 10.5198 | 10.5714 | 10.5629 | 10.5416 | 10.6336 | 10.7364 | 10.7879 | 10.846 | 10.846 | 10.846 | 10.846 | 10.846 | 10.846
OCGT - Without CCS (NNS) | High | 5.6761 | 5.7657 | 7.191 | 8.3484 | 8.2747 | 8.7358 | 9.0173 | 9.0271 | 9.0181 | 9.0086 | 9.142 | 9.3652 | 9.4931 | 9.5338 | 9.5494 | 9.5661 | 9.5916 | 9.7048 | 9.8474 | 9.8989 | 9.8904 | 9.8691 | 9.9641 | 10.0729 | 10.1306 | 10.1918 | 10.1918 | 10.1918 | 10.1918 | 10.1918 | 10.1918
OCGT - Without CCS (NQ) | High | 6.9131 | 6.9088 | 6.9046 | 6.9003 | 6.8961 | 6.8919 | 6.8877 | 6.8836 | 6.8794 | 6.9911 | 7.1028 | 7.4349 | 8.3274 | 8.9025 | 8.9171 | 8.9222 | 9.0684 | 9.2381 | 9.2986 | 9.3245 | 9.3182 | 9.3088 | 9.392 | 9.4985 | 9.5056 | 9.4966 | 9.4966 | 9.4966 | 9.4966 | 9.4966 | 9.4966
OCGT - Without CCS (NSA) | High | 6.8122 | 7.8775 | 8.7547 | 8.31 | 8.0544 | 8.6799 | 9.6187 | 10.0637 | 9.8735 | 9.7411 | 9.7341 | 9.8124 | 9.9688 | 10.0595 | 10.0727 | 10.0762 | 10.2209 | 10.3891 | 10.448 | 10.4725 | 10.4648 | 10.4543 | 10.5366 | 10.6141 | 10.6167 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314 | 10.6314
OCGT - Without CCS (NVIC) | High | 6.5296 | 7.3735 | 8.219 | 8.025 | 8.0284 | 8.4993 | 9.0513 | 9.3315 | 9.3315 | 9.3315 | 9.4749 | 9.7073 | 9.8441 | 9.894 | 9.9183 | 9.9443 | 9.9787 | 10.1003 | 10.2517 | 10.3122 | 10.3122 | 10.298 | 10.3959 | 10.5045 | 10.5618 | 10.6226 | 10.6226 | 10.6226 | 10.6226 | 10.6226 | 10.6226
OCGT - Without CCS (SEQ) | High | 5.8676 | 7.7422 | 9.333 | 8.8881 | 8.4392 | 8.5553 | 8.9934 | 9.2572 | 9.0733 | 8.9472 | 8.9466 | 9.0311 | 9.3445 | 9.5913 | 9.6091 | 9.6172 | 9.7664 | 9.9393 | 10.0027 | 10.0316 | 10.0284 | 10.0253 | 10.1181 | 10.2059 | 10.2184 | 10.2381 | 10.2381 | 10.2381 | 10.2381 | 10.2381 | 10.2381
OCGT - Without CCS (SESA) | High | 6.6935 | 7.5298 | 8.3678 | 8.1664 | 8.1624 | 8.6259 | 9.1706 | 9.4435 | 9.4363 | 9.4291 | 9.5652 | 9.7905 | 9.9203 | 9.9632 | 9.9806 | 9.9995 | 10.1154 | 10.313 | 10.3915 | 10.3847 | 10.378 | 10.4242 | 10.5837 | 10.6877 | 10.7296 | 10.7774 | 10.7774 | 10.7774 | 10.7774 | 10.7774 | 10.7774
OCGT - Without CCS (SWNSW) | High | 7.2304 | 8.1004 | 8.9424 | 8.6987 | 8.6486 | 9.1621 | 9.7607 | 10.0374 | 10.034 | 10.0306 | 10.1705 | 10.3894 | 10.5228 | 10.5795 | 10.6005 | 10.6231 | 10.6542 | 10.7725 | 10.9206 | 10.9779 | 10.9746 | 10.9507 | 11.0327 | 11.1258 | 11.1316 | 11.1488 | 11.1488 | 11.1488 | 11.1488 | 11.1488 | 11.1488
OCGT - Without CCS (SWQ) | High | 5.5821 | 7.2548 | 8.7065 | 8.2666 | 7.8886 | 8.0753 | 8.4468 | 8.712 | 8.5977 | 8.473 | 8.4739 | 8.5599 | 8.8747 | 9.1229 | 9.1422 | 9.1517 | 9.3024 | 9.4766 | 9.5415 | 9.5718 | 9.57 | 9.5732 | 9.6771 | 9.8038 | 9.8307 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314 | 9.8314
OCGT - Without CCS (TAS) | High | 6.4132 | 7.2571 | 8.1025 | 7.9086 | 7.912 | 8.3828 | 8.9349 | 9.2151 | 9.2151 | 9.2151 | 9.3584 | 9.5908 | 9.7277 | 9.7775 | 9.8019 | 9.8278 | 9.8622 | 9.9838 | 10.1352 | 10.1958 | 10.1958 | 10.1829 | 10.2837 | 10.395 | 10.455 | 10.5172 | 10.5172 | 10.5172 | 10.5172 | 10.5172 | 10.5172
CCGT - Without CCS (ADE) | Low | 5.8112 | 6.5903 | 7.5736 | 7.8591 | 8.2782 | 9.0314 | 9.5573 | 9.953 | 10.3433 | 10.8259 | 11.3238 | 11.5215 | 11.5783 | 11.6315 | 11.6866 | 11.9494 | 12.2954 | 12.5984 | 12.9045 | 13.1013 | 13.1562 | 13.1552 | 13.244 | 13.3143 | 13.2791 | 13.2616 | 13.2616 | 13.2616 | 13.2616 | 13.2616 | 13.2616
CCGT - Without CCS (CAN) | Low | 6.3571 | 7.4602 | 8.2808 | 9.0456 | 9.7572 | 10.062 | 10.3018 | 10.6763 | 10.8922 | 11.0342 | 11.2822 | 11.3947 | 11.4509 | 11.5036 | 11.5581 | 11.82 | 12.1655 | 12.4681 | 12.747 | 12.8615 | 12.8635 | 12.9297 | 13.1006 | 13.2318 | 13.2536 | 13.2498 | 13.2498 | 13.2498 | 13.2498 | 13.2498 | 13.2498
CCGT - Without CCS (CQ) | Low | 6.6122 | 9.1627 | 10.9648 | 11.5375 | 11.9584 | 12.1703 | 12.2537 | 12.2586 | 12.2633 | 12.2677 | 12.272 | 12.2762 | 12.2802 | 12.2839 | 12.2876 | 12.291 | 12.2944 | 12.2976 | 12.3006 | 12.3034 | 12.3047 | 12.2991 | 12.2885 | 12.2782 | 12.2681 | 12.2631 | 12.2631 | 12.2631 | 12.2631 | 12.2631 | 12.2631
CCGT - Without CCS (CVIC) | Low | 5.4137 | 6.1977 | 7.1858 | 7.4762 | 7.9 | 8.658 | 9.1887 | 9.5891 | 9.984 | 10.4713 | 10.9738 | 11.1762 | 11.2375 | 11.2952 | 11.3547 | 11.622 | 11.9726 | 12.2799 | 12.5638 | 12.6833 | 12.6902 | 12.7608 | 12.9358 | 13.071 | 13.2372 | 13.3758 | 13.3758 | 13.3758 | 13.3758 | 13.3758 | 13.3758
CCGT - Without CCS (LV) | Low | 4.8043 | 5.5901 | 6.58 | 6.8721 | 7.2977 | 8.0575 | 8.5899 | 8.992 | 9.3003 | 9.7008 | 10.205 | 10.4091 | 10.4721 | 10.5314 | 10.5927 | 10.8616 | 11.2138 | 11.5228 | 11.8083 | 11.9294 | 11.938 | 12.0185 | 12.2116 | 12.3645 | 12.548 | 12.6951 | 12.6951 | 12.6951 | 12.6951 | 12.6951 | 12.6951
CCGT - Without CCS (MEL) | Low | 5.2259 | 6.0117 | 7.0016 | 7.2937 | 7.7193 | 8.479 | 9.0114 | 9.4136 | 9.7218 | 10.1223 | 10.6265 | 10.8306 | 10.8936 | 10.9529 | 11.0142 | 11.2832 | 11.6353 | 11.9443 | 12.2299 | 12.351 | 12.3595 | 12.4349 | 12.6178 | 12.7608 | 12.9346 | 13.0769 | 13.0769 | 13.0769 | 13.0769 | 13.0769 | 13.0769
CCGT - Without CCS (NCEN) | Low | 6.7482 | 7.8491 | 8.6674 | 9.4298 | 10.1388 | 10.4414 | 10.6788 | 11.0509 | 11.2646 | 11.4044 | 11.6501 | 11.7604 | 11.8145 | 11.8647 | 11.9172 | 12.1769 | 12.5202 | 12.8208 | 13.0975 | 13.2096 | 13.2096 | 13.2096 | 13.2067 | 13.2007 | 13.1945 | 13.1914 | 13.1914 | 13.1914 | 13.1914 | 13.1914 | 13.1914
CCGT - Without CCS (NNS) | Low | 5.4801 | 5.6486 | 7.2218 | 9.6911 | 10.8112 | 11.1138 | 11.1923 | 11.1923 | 11.1923 | 11.1923 | 11.1923 | 11.1923 | 11.1923 | 11.1923 | 11.2447 | 11.5044 | 11.8477 | 12.1483 | 12.425 | 12.5372 | 12.5372 | 12.5372 | 12.5372 | 12.5372 | 12.5372 | 12.5372 | 12.5372 | 12.5372 | 12.5372 | 12.5372 | 12.5372
CCGT - Without CCS (NQ) | Low | 6.9304 | 6.9262 | 6.9219 | 8.8827 | 10.999 | 11.1481 | 11.1416 | 11.3364 | 11.5315 | 11.5277 | 11.5239 | 11.5201 | 11.5164 | 11.5293 | 11.5568 | 11.5676 | 11.5636 | 11.5597 | 11.5557 | 11.5518 | 11.5479 | 11.5363 | 11.5171 | 11.4985 | 11.4802 | 11.4712 | 11.4712 | 11.4712 | 11.4712 | 11.4712 | 11.4712
CCGT - Without CCS (NSA) | Low | 6.3989 | 8.3132 | 9.9431 | 10.6208 | 11.3317 | 11.7147 | 11.9411 | 12.3022 | 12.51 | 12.6439 | 12.8837 | 12.984 | 12.9771 | 12.9703 | 12.9637 | 12.957 | 12.9503 | 12.9437 | 13.0509 | 13.1596 | 13.1562 | 13.1552 | 13.244 | 13.3143 | 13.2791 | 13.2616 | 13.2616 | 13.2616 | 13.2616 | 13.2616 | 13.2616
CCGT - Without CCS (NVIC) | Low | 5.8254 | 6.6111 | 7.601 | 8.284 | 9.0002 | 9.3947 | 9.6365 | 10.0131 | 10.3213 | 10.7218 | 11.226 | 11.4301 | 11.4931 | 11.5524 | 11.6137 | 11.8826 | 12.2348 | 12.5438 | 12.8293 | 12.9505 | 12.959 | 13.0271 | 13.1956 | 13.3245 | 13.4845 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62 | 13.62
CCGT - Without CCS (SEQ) | Low | 6.1872 | 8.5681 | 10.3748 | 11.0525 | 11.6467 | 12.0384 | 12.2058 | 12.2052 | 12.2045 | 12.2039 | 12.2033 | 12.2027 | 12.2021 | 12.2181 | 12.2488 | 12.2626 | 12.3785 | 12.4939 | 12.4918 | 12.4898 | 12.4877 | 12.4791 | 12.4641 | 12.4495 | 12.4353 | 12.4282 | 12.4282 | 12.4282 | 12.4282 | 12.4282 | 12.4282
CCGT - Without CCS (SESA) | Low | 5.9892 | 6.7675 | 7.7499 | 8.0345 | 8.4527 | 9.2051 | 9.7301 | 10.125 | 10.5145 | 10.9962 | 11.4933 | 11.6902 | 11.7461 | 11.7985 | 11.8529 | 12.1148 | 12.46 | 12.7622 | 13.0675 | 13.2635 | 13.3176 | 13.3143 | 13.3992 | 13.5077 | 13.6632 | 13.7966 | 13.7966 | 13.7966 | 13.7966 | 13.7966 | 13.7966
CCGT - Without CCS (SWNSW) | Low | 6.5261 | 7.3381 | 8.3244 | 9.0039 | 9.7165 | 10.1076 | 10.3459 | 10.719 | 11.0237 | 11.4209 | 11.9217 | 12.1224 | 12.182 | 12.2379 | 12.2959 | 12.5615 | 12.9104 | 13.216 | 13.4983 | 13.6161 | 13.6214 | 13.6684 | 13.7039 | 13.6858 | 13.6678 | 13.6588 | 13.6588 | 13.6588 | 13.6588 | 13.6588 | 13.6588
CCGT - Without CCS (SWQ) | Low | 5.9017 | 8.1707 | 9.9976 | 10.7001 | 11.2954 | 11.5795 | 11.5906 | 11.6599 | 11.7289 | 11.7298 | 11.7306 | 11.7314 | 11.7323 | 11.7498 | 11.7818 | 11.7971 | 11.9145 | 12.0312 | 12.0306 | 12.03 | 12.0294 | 12.0271 | 12.0231 | 12.0193 | 12.0155 | 12.0136 | 12.0136 | 12.0136 | 12.0136 | 12.0136 | 12.0136
CCGT - Without CCS (TAS) | Low | 5.7089 | 6.4947 | 7.4846 | 7.7767 | 8.2023 | 8.9621 | 9.4944 | 9.8966 | 10.2048 | 10.6054 | 11.1096 | 11.3136 | 11.3766 | 11.436 | 11.4972 | 11.7662 | 12.1184 | 12.4273 | 12.7129 | 12.834 | 12.8425 | 12.9121 | 13.0833 | 13.215 | 13.3777 | 13.5146 | 13.5146 | 13.5146 | 13.5146 | 13.5146 | 13.5146
OCGT - Without CCS (ADE) | Low | 7.8112 | 8.5903 | 9.5736 | 9.8591 | 10.2782 | 11.0314 | 11.5573 | 11.953 | 12.3433 | 12.8259 | 13.3238 | 13.5215 | 13.5783 | 13.6315 | 13.6866 | 13.9494 | 14.2954 | 14.5984 | 14.9045 | 15.1013 | 15.1562 | 15.1552 | 15.244 | 15.3143 | 15.2791 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616
OCGT - Without CCS (CAN) | Low | 8.3571 | 9.4602 | 10.2808 | 11.0456 | 11.7572 | 12.062 | 12.3018 | 12.6763 | 12.8922 | 13.0342 | 13.2822 | 13.3947 | 13.4509 | 13.5036 | 13.5581 | 13.82 | 14.1655 | 14.4681 | 14.747 | 14.8615 | 14.8635 | 14.9297 | 15.1006 | 15.2318 | 15.2536 | 15.2498 | 15.2498 | 15.2498 | 15.2498 | 15.2498 | 15.2498
OCGT - Without CCS (CQ) | Low | 8.6122 | 11.1627 | 12.9648 | 13.5375 | 13.9584 | 14.1703 | 14.2537 | 14.2586 | 14.2633 | 14.2677 | 14.272 | 14.2762 | 14.2802 | 14.2839 | 14.2876 | 14.291 | 14.2944 | 14.2976 | 14.3006 | 14.3034 | 14.3047 | 14.2991 | 14.2885 | 14.2782 | 14.2681 | 14.2631 | 14.2631 | 14.2631 | 14.2631 | 14.2631 | 14.2631
OCGT - Without CCS (CVIC) | Low | 7.4137 | 8.1977 | 9.1858 | 9.4762 | 9.9 | 10.658 | 11.1887 | 11.5891 | 11.984 | 12.4713 | 12.9738 | 13.1762 | 13.2375 | 13.2952 | 13.3547 | 13.622 | 13.9726 | 14.2799 | 14.5638 | 14.6833 | 14.6902 | 14.7608 | 14.9358 | 15.071 | 15.2372 | 15.3758 | 15.3758 | 15.3758 | 15.3758 | 15.3758 | 15.3758
OCGT - Without CCS (LV) | Low | 6.8043 | 7.5901 | 8.58 | 8.8721 | 9.2977 | 10.0575 | 10.5899 | 10.992 | 11.3003 | 11.7008 | 12.205 | 12.4091 | 12.4721 | 12.5314 | 12.5927 | 12.8616 | 13.2138 | 13.5228 | 13.8083 | 13.9294 | 13.938 | 14.0185 | 14.2116 | 14.3645 | 14.548 | 14.6951 | 14.6951 | 14.6951 | 14.6951 | 14.6951 | 14.6951
OCGT - Without CCS (MEL) | Low | 7.2259 | 8.0117 | 9.0016 | 9.2937 | 9.7193 | 10.479 | 11.0114 | 11.4136 | 11.7218 | 12.1223 | 12.6265 | 12.8306 | 12.8936 | 12.9529 | 13.0142 | 13.2832 | 13.6353 | 13.9443 | 14.2299 | 14.351 | 14.3595 | 14.4349 | 14.6178 | 14.7608 | 14.9346 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769 | 15.0769
OCGT - Without CCS (NCEN) | Low | 8.7482 | 9.8491 | 10.6674 | 11.4298 | 12.1388 | 12.4414 | 12.6788 | 13.0509 | 13.2646 | 13.4044 | 13.6501 | 13.7604 | 13.8145 | 13.8647 | 13.9172 | 14.1769 | 14.5202 | 14.8208 | 15.0975 | 15.2096 | 15.2096 | 15.2096 | 15.2067 | 15.2007 | 15.1945 | 15.1914 | 15.1914 | 15.1914 | 15.1914 | 15.1914 | 15.1914
OCGT - Without CCS (NNS) | Low | 7.4801 | 7.6486 | 9.2218 | 11.6911 | 12.8112 | 13.1138 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.2447 | 13.5044 | 13.8477 | 14.1483 | 14.425 | 14.5372 | 14.5372 | 14.5372 | 14.5372 | 14.5372 | 14.5372 | 14.5372 | 14.5372 | 14.5372 | 14.5372 | 14.5372 | 14.5372
OCGT - Without CCS (NQ) | Low | 8.9304 | 8.9262 | 8.9219 | 10.8827 | 12.999 | 13.1481 | 13.1416 | 13.3364 | 13.5315 | 13.5277 | 13.5239 | 13.5201 | 13.5164 | 13.5293 | 13.5568 | 13.5676 | 13.5636 | 13.5597 | 13.5557 | 13.5518 | 13.5479 | 13.5363 | 13.5171 | 13.4985 | 13.4802 | 13.4712 | 13.4712 | 13.4712 | 13.4712 | 13.4712 | 13.4712
OCGT - Without CCS (NSA) | Low | 8.3989 | 10.3132 | 11.9431 | 12.6208 | 13.3317 | 13.7147 | 13.9411 | 14.3022 | 14.51 | 14.6439 | 14.8837 | 14.984 | 14.9771 | 14.9703 | 14.9637 | 14.957 | 14.9503 | 14.9437 | 15.0509 | 15.1596 | 15.1562 | 15.1552 | 15.244 | 15.3143 | 15.2791 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616 | 15.2616
OCGT - Without CCS (NVIC) | Low | 7.8254 | 8.6111 | 9.601 | 10.284 | 11.0002 | 11.3947 | 11.6365 | 12.0131 | 12.3213 | 12.7218 | 13.226 | 13.4301 | 13.4931 | 13.5524 | 13.6137 | 13.8826 | 14.2348 | 14.5438 | 14.8293 | 14.9505 | 14.959 | 15.0271 | 15.1956 | 15.3245 | 15.4845 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62 | 15.62
OCGT - Without CCS (SEQ) | Low | 8.1872 | 10.5681 | 12.3748 | 13.0525 | 13.6467 | 14.0384 | 14.2058 | 14.2052 | 14.2045 | 14.2039 | 14.2033 | 14.2027 | 14.2021 | 14.2181 | 14.2488 | 14.2626 | 14.3785 | 14.4939 | 14.4918 | 14.4898 | 14.4877 | 14.4791 | 14.4641 | 14.4495 | 14.4353 | 14.4282 | 14.4282 | 14.4282 | 14.4282 | 14.4282 | 14.4282
OCGT - Without CCS (SESA) | Low | 7.9892 | 8.7675 | 9.7499 | 10.0345 | 10.4527 | 11.2051 | 11.7301 | 12.125 | 12.5145 | 12.9962 | 13.4933 | 13.6902 | 13.7461 | 13.7985 | 13.8529 | 14.1148 | 14.46 | 14.7622 | 15.0675 | 15.2635 | 15.3176 | 15.3143 | 15.3992 | 15.5077 | 15.6632 | 15.7966 | 15.7966 | 15.7966 | 15.7966 | 15.7966 | 15.7966
OCGT - Without CCS (SWNSW) | Low | 8.5261 | 9.3381 | 10.3244 | 11.0039 | 11.7165 | 12.1076 | 12.3459 | 12.719 | 13.0237 | 13.4209 | 13.9217 | 14.1224 | 14.182 | 14.2379 | 14.2959 | 14.5615 | 14.9104 | 15.216 | 15.4983 | 15.6161 | 15.6214 | 15.6684 | 15.7039 | 15.6858 | 15.6678 | 15.6588 | 15.6588 | 15.6588 | 15.6588 | 15.6588 | 15.6588
OCGT - Without CCS (SWQ) | Low | 7.9017 | 10.1707 | 11.9976 | 12.7001 | 13.2954 | 13.5795 | 13.5906 | 13.6599 | 13.7289 | 13.7298 | 13.7306 | 13.7314 | 13.7323 | 13.7498 | 13.7818 | 13.7971 | 13.9145 | 14.0312 | 14.0306 | 14.03 | 14.0294 | 14.0271 | 14.0231 | 14.0193 | 14.0155 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136 | 14.0136
OCGT - Without CCS (TAS) | Low | 7.7089 | 8.4947 | 9.4846 | 9.7767 | 10.2023 | 10.9621 | 11.4944 | 11.8966 | 12.2048 | 12.6054 | 13.1096 | 13.3136 | 13.3766 | 13.436 | 13.4972 | 13.7662 | 14.1184 | 14.4273 | 14.7129 | 14.834 | 14.8425 | 14.9121 | 15.0833 | 15.215 | 15.3777 | 15.5146 | 15.5146 | 15.5146 | 15.5146 | 15.5146 | 15.5146

## New Technologies
Technical parameters and operating costs by technology (costs in 2014-15 $)
Technology | Fuel Type | First Year Assumed Commercially Viable | Economic Life | Min Gen (%) | Auxiliary load (%) | Hot Day Derate factor | No Load Fuel Consumption (% of Full Load Fuel Consumption) | Ramp Up Rate (MW/h) | Ramp Down Rate (MW/h) | Fugitive Emissions (Scope 3) (kg CO2e/GJ) | Combustion Emissions (Scope 1) (tonnes CO2e/GJ) | Emissions Capture (%) | Thermal Efficiency (Sent-out HHV %) | Pumping Efficiency (GWh pumped per GWh generated) - within 24 hours | Pumping Efficiency ( GWh pumped per GWh generated) - annual | Maintenance (days/yr) | Fixed Op Cost ($/MW/year) | Variable Op Cost ($/MWh sent-out) | Cold Start-up Notificatio nTime (Hr) | Warm Start-up Notificatio nTime (Hr) | Hot Start-up Notificatio nTime (Hr) | Cold Start-up Costs ($/MW sent-out) | Warm Start-up Costs ($/MW sent-out) | Hot Start-up Costs ($/MW sent-out) | Retirement/Rehabilation Cost ($/MW)
Biomass | Biomass | 2014 | 30 | 40 | 8 | 0.005 | 0.1 | 20 | 20 | See below | See below | 0 | 27.67% | 0 | 0 | 30 | 125000 | 8 | 24 | 4 | 2 | 200 | 100 | 40 | 30000
CCGT - With CCS | Natural Gas | 2024 | 40 | 0 | 10 | 12 | 0.3 | 600 | 600 | See below | See below | 85 | 44.12% | 0 | 0 | 20 | 17000 | 12 | 15 | 3 | 1 | 25 | 15 | 5 | 10000
CCGT - Without CCS | Natural Gas | 2014 | 40 | 0 | 3 | 13 | 0.3 | 600 | 600 | See below | See below | 0 | 50.61% | 0 | 0 | 20 | 10000 | 7 | 15 | 3 | 1 | 25 | 15 | 5 | 10000
Integrated Solar Combined Cycle (ISCS) | Natural Gas | 2016 | 40 | 40 | 5 | 13 | 0.3 | 600 | 600 | See below | See below | 0 | 53.7% | 0 | 0 | 20 | 15000 | 10 | 12 | 2 | 1 | 10 | 5 | 3 | 15000
Large Scale Battery Storage | N/A | 2016 | 10 | 0 | 0.5 | 0 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 10 | 30000 | 6 | 1 | 1 | 1 | 0 | 0 | 0 | 5000
OCGT - Without CCS | Natural Gas | 2014 | 30 | 0 | 1 | 15 | 0.3 | 1200 | 1200 | See below | See below | 0 | 34.55% | 0 | 0 | 2.5 | 4000 | 10 | 6 | 1 | 1 | 100 | 100 | 100 | 5000
Pumped Hydro Storage | N/A | 2014 | 50 | 0 | 1 | 0 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 1.7 | 1.7 | 10 | 5000 | 5 | 2 | 1 | 1 | 0 | 0 | 0 | 100000
Solar PV SAT | N/A | 2014 | 25 | 0 | 1 | 2 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 5 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20000
Solar PV DAT | N/A | 2014 | 25 | 0 | 1 | 2 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 5 | 39000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20000
Solar PV FFP | N/A | 2014 | 25 | 0 | 1 | 2 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 5 | 25000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20000
Solar Thermal CLF | N/A | 2016 | 25 | 10 | 8 | 5 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 10 | 64000 | 15.2 | 5 | 3 | 1 | 5 | 3 | 2 | 25000
Solar Thermal CR WS | N/A | 2016 | 25 | 10 | 10 | 5 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 12 | 72000 | 5.7 | 5 | 3 | 1 | 10 | 5 | 2 | 25000
Solar Thermal PT WS | N/A | 2016 | 25 | 10 | 10 | 5 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 12 | 73000 | 11.4 | 5 | 3 | 1 | 10 | 5 | 2 | 25000
Supercritical PC - Black coal with CCS | Black Coal | 2024 | 50 | 40 | 18.5 | 2 | 0.1 | 900 | 900 | See below | See below | 90 | 31.42% | 0 | 0 | 30 | 73200 | 9 | 24 | 4 | 2 | 350 | 120 | 40 | 50000
Supercritical PC - Black coal without CCS | Brown Coal | 2014 | 50 | 40 | 7.1 | 0.5 | 0.1 | 900 | 900 | See below | See below | 0 | 41.52% | 0 | 0 | 30 | 50500 | 4 | 24 | 4 | 2 | 350 | 120 | 40 | 50000
Supercritical PC - Brown coal with CCS | Black Coal | 2024 | 50 | 40 | 24.3 | 2 | 0.1 | 900 | 900 | See below | See below | 90 | 20.75% | 0 | 0 | 30 | 96500 | 11 | 48 | 4 | 2 | 350 | 120 | 40 | 80000
Supercritical PC - Brown coal without CCS | Brown Coal | 2014 | 50 | 40 | 9.6 | 0.5 | 0.1 | 900 | 900 | See below | See below | 0 | 28.85% | 0 | 0 | 30 | 65500 | 5 | 48 | 4 | 2 | 350 | 120 | 40 | 80000
Wind - (100 MW) | N/A | 2014 | 20 | 0 | 1 | 0 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 3 | 45000 | 15 | 0 | 0 | 0 | 5 | 3 | 2 | 10000
Wave/Ocean | N/A | 2020 | 20 | 0 | 0.5 | 0 | 0 | 10000 | 10000 | See below | See below | 0 | 100% | 0 | 0 | 10 | 40000 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 10000
Planned Maintenance Rates (days per year)
Technology | QLD | NSW | VIC | SA | TAS | 0 = N/A
Biomass | 30 | 30 | 30 | 0 | 30
CCGT - With CCS | 20 | 20 | 20 | 0 | 0
CCGT - Without CCS | 20 | 20 | 20 | 20 | 20
Integrated Solar Combined Cycle (ISCS) | 15 | 15 | 15 | 15 | 0
Large Scale Battery Storage | 10 | 10 | 10 | 10 | 10
OCGT - Without CCS | 3 | 3 | 3 | 3 | 3
Pumped Hydro Storage | 10 | 10 | 10 | 10 | 10
Solar PV SAT | 5 | 5 | 5 | 5 | 0
Solar PV DAT | 5 | 5 | 5 | 5 | 0
Solar PV FFP | 5 | 5 | 5 | 5 | 0
Solar Thermal CLF | 10 | 10 | 10 | 10 | 0
Solar Thermal CR WS | 12 | 12 | 12 | 12 | 0
Solar Thermal PT WS | 12 | 12 | 12 | 12 | 0
Supercritical PC - Black coal with CCS | 30 | 30 | 0 | 0 | 0
Supercritical PC - Black coal without CCS | 30 | 30 | 0 | 0 | 0
Supercritical PC - Brown coal with CCS | 0 | 0 | 30 | 0 | 0
Supercritical PC - Brown coal without CCS | 0 | 0 | 30 | 0 | 0
Wind - (100 MW) | 3 | 3 | 3 | 3 | 3
Wave/Ocean | 0 | 10 | 10 | 0 | 0
Forced Outage Rates
Transition Matrix (average hours between transitions)
Technology | Available To Partial | Available to Unavailable | Partial to Available | Partial to Unavailable | Unavailable to Available | Unavailable to Partial | Partial Derating (%) | Full Forced Outage Rate (%) | Partial Outage Rate (%)
Biomass | 200 | 1500 | 20 | 8000 | 50 | 4000 | 30 | 3 | 10
CCGT - With CCS | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 50 | 4 | 1
CCGT - Without CCS | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 50 | 2 | 1
Integrated Solar Combined Cycle (ISCS) | 2100.04 | 464.04 | 14.57 | 380.44 | 16.89 | 10796991893 | 50 | 4 | 1
Large Scale Battery Storage | 8000 | 16000 | 40000 | 40000 | 100 | 10000 | 20 | 1 | 0.5
OCGT - Without CCS | 1754.31 | 89.55 | 26.85 | 23890870078 | 30.2 | 243444.67 | 40 | 2 | 1
Pumped Hydro Storage | 49250.18 | 477.8 | 1240.51 | 6661.55 | 17.8 | 271658.01 | 30 | 3.52 | 2.02
Solar PV SAT | 500 | 10000 | 10000 | 12000 | 600 | 800 | 15 | 2 | 1
Solar PV DAT | 500 | 10000 | 10000 | 12000 | 600 | 800 | 15 | 2 | 1
Solar PV FFP | 500 | 10000 | 10000 | 12000 | 600 | 800 | 15 | 2 | 1
Solar Thermal CLF | 200 | 1500 | 20 | 8000 | 50 | 4000 | 30 | 3 | 10
Solar Thermal CR WS | 200 | 1500 | 20 | 8000 | 50 | 4000 | 30 | 3 | 10
Solar Thermal PT WS | 200 | 1500 | 20 | 8000 | 50 | 4000 | 30 | 3 | 10
Supercritical PC - Black coal with CCS | 200 | 1500 | 20 | 8000 | 50 | 4000 | 30 | 4 | 8
Supercritical PC - Black coal without CCS | 200 | 1500 | 20 | 8000 | 50 | 4000 | 30 | 2.5 | 6
Supercritical PC - Brown coal with CCS | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 30 | 5 | 10
Supercritical PC - Brown coal without CCS | 35.9 | 423 | 6.42 | 54546.88 | 16.35 | 67168.59 | 30 | 3 | 10
Wind - (100 MW) | 500 | 10000 | 10000 | 12000 | 600 | 800 | 15 | 5 | 20
Wave/Ocean | 200 | 1500 | 20 | 8000 | 50 | 4000 | 30 | 3 | 10
Scope 1 emission factors (kg CO2-e/GJ of fuel)
Technology | QLD | NSW | VIC | SA | TAS
Biomass | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
CCGT - With CCS | 58 | 50 | 53 | 57 | 56
CCGT - Without CCS | 58 | 50 | 53 | 57 | 56
Integrated Solar Combined Cycle (ISCS) | 58 | 50 | 53 | 57 | 56
Large Scale Battery Storage | 0 | 0 | 0 | 0 | 0
OCGT - Without CCS | 58 | 50 | 53 | 57 | 56
Pumped Hydro Storage | 0 | 0 | 0 | 0 | 0
Solar PV SAT | 0 | 0 | 0 | 0 | 0
Solar PV DAT | 0 | 0 | 0 | 0 | 0
Solar PV FFP | 0 | 0 | 0 | 0 | 0
Solar Thermal CLF | 0 | 0 | 0 | 0 | 0
Solar Thermal CR WS | 0 | 0 | 0 | 0 | 0
Solar Thermal PT WS | 0 | 0 | 0 | 0 | 0
Supercritical PC - Black coal with CCS | 93 | 91 | NA | NA | NA
Supercritical PC - Black coal without CCS | 93 | 91 | NA | NA | NA
Supercritical PC - Brown coal with CCS | NA | NA | 97 | NA | NA
Supercritical PC - Brown coal without CCS | NA | NA | 97 | NA | NA
Wind - (100 MW) | 0 | 0 | 0 | 0 | 0
Wave/Ocean | 0 | 0 | 0 | 0 | 0
Scope 3 emission factors (kg CO2-e/GJ of fuel)
Technology | QLD | NSW | VIC | SA | TAS
Biomass | 0 | 0 | 0 | 0 | 0
CCGT - With CCS | 7.6 | 13.5 | 3.9 | 10.2 | 0
CCGT - Without CCS | 7.6 | 13.5 | 3.9 | 10.2 | 0
Integrated Solar Combined Cycle (ISCS) | 7.6 | 13.5 | 3.9 | 10.2 | 0
Large Scale Battery Storage | 0 | 0 | 0 | 0 | 0
OCGT - Without CCS | 7.6 | 13.5 | 3.9 | 10.2 | 0
Pumped Hydro Storage | 0 | 0 | 0 | 0 | 0
Solar PV SAT | 0 | 0 | 0 | 0 | 0
Solar PV DAT | 0 | 0 | 0 | 0 | 0
Solar PV FFP | 0 | 0 | 0 | 0 | 0
Solar Thermal CLF | 0 | 0 | 0 | 0 | 0
Solar Thermal CR WS | 0 | 0 | 0 | 0 | 0
Solar Thermal PT WS | 0 | 0 | 0 | 0 | 0
Supercritical PC - Black coal with CCS | 2.3 | 9.2 | NA | NA | NA
Supercritical PC - Black coal without CCS | 2.3 | 9.2 | NA | NA | NA
Supercritical PC - Brown coal with CCS | NA | NA | 0.4 | NA | NA
Supercritical PC - Brown coal without CCS | NA | NA | 0.4 | NA | NA
Wind - (100 MW) | 0 | 0 | 0 | 0 | 0
Wave/Ocean | 0 | 0 | 0 | 0 | 0

## New Thermal Efficiency
Thermal Efficiency (%, HHV, sent-out) for New Units - based on year of construction
Year Ending June
Technology | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Biomass | 27.67 | 27.9332 | 28.186 | 28.4286 | 28.6613 | 28.8845 | 29.0985 | 29.3036 | 29.5 | 29.6881 | 29.8682 | 30.0405 | 30.2053 | 30.363 | 30.5138 | 30.6579 | 30.7957 | 30.9273 | 31.0531 | 31.1732 | 31.2878 | 31.3973 | 31.5018 | 31.6016 | 31.6968 | 31.7876 | 31.8742 | 31.9568 | 32.0356 | 32.1108 | 32.1824
CCGT - With CCS | 44.12 | 44.5355 | 44.9305 | 45.3058 | 45.6622 | 46.0005 | 46.3214 | 46.6257 | 46.9143 | 47.1876 | 47.4466 | 47.6918 | 47.924 | 48.1437 | 48.3515 | 48.5481 | 48.734 | 48.9097 | 49.0758 | 49.2328 | 49.3811 | 49.5211 | 49.6534 | 49.7783 | 49.8963 | 50.0076 | 50.1127 | 50.2119 | 50.3054 | 50.3937 | 50.477
CCGT - Without CCS | 50.61 | 51.0772 | 51.5124 | 51.9177 | 52.2947 | 52.6452 | 52.971 | 53.2735 | 53.5544 | 53.8151 | 54.0569 | 54.2811 | 54.489 | 54.6816 | 54.86 | 55.0252 | 55.1782 | 55.3198 | 55.4509 | 55.5722 | 55.6844 | 55.7882 | 55.8841 | 55.9729 | 56.055 | 56.1308 | 56.2009 | 56.2658 | 56.3257 | 56.381 | 56.4322
Integrated Solar Combined Cycle (ISCS) | 53.7 | 54.1373 | 54.5362 | 54.8998 | 55.231 | 55.5325 | 55.8068 | 56.0562 | 56.2829 | 56.4889 | 56.6759 | 56.8457 | 56.9998 | 57.1396 | 57.2664 | 57.3814 | 57.4857 | 57.5802 | 57.6659 | 57.7435 | 57.8138 | 57.8775 | 57.9353 | 57.9875 | 58.0349 | 58.0777 | 58.1166 | 58.1517 | 58.1835 | 58.2124 | 58.2384
Large Scale Battery Storage | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
OCGT - Without CCS | 34.55 | 34.8721 | 35.1753 | 35.4604 | 35.7284 | 35.9802 | 36.2166 | 36.4385 | 36.6466 | 36.8418 | 37.0248 | 37.1962 | 37.3568 | 37.5071 | 37.6479 | 37.7796 | 37.9029 | 38.0182 | 38.1261 | 38.2269 | 38.3212 | 38.4093 | 38.4916 | 38.5686 | 38.6404 | 38.7076 | 38.7703 | 38.8289 | 38.8836 | 38.9346 | 38.9823
Pumped Hydro Storage | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Solar PV SAT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Solar PV DAT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Solar PV FFP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Solar Thermal CLF | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Solar Thermal CR WS | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Solar Thermal PT WS | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Supercritical PC - Black coal with CCS | 31.24 | 31.5432 | 31.8402 | 32.1312 | 32.4162 | 32.6952 | 32.9683 | 33.2355 | 33.497 | 33.7527 | 34.0027 | 34.2472 | 34.4861 | 34.7196 | 34.9477 | 35.1706 | 35.3882 | 35.6007 | 35.8082 | 36.0107 | 36.2083 | 36.4012 | 36.5893 | 36.7728 | 36.9518 | 37.1264 | 37.2965 | 37.4625 | 37.6242 | 37.7818 | 37.9354
Supercritical PC - Brown coal with CCS | 20.75 | 21.1389 | 21.5101 | 21.8641 | 22.2013 | 22.5221 | 22.8271 | 23.1167 | 23.3916 | 23.6522 | 23.8992 | 24.133 | 24.3543 | 24.5635 | 24.7612 | 24.948 | 25.1244 | 25.2908 | 25.4478 | 25.5958 | 25.7353 | 25.8668 | 25.9906 | 26.1072 | 26.2169 | 26.3201 | 26.4173 | 26.5086 | 26.5945 | 26.6753 | 26.7512
Supercritical PC - Black coal without CCS | 41.52 | 41.9071 | 42.2715 | 42.6141 | 42.9362 | 43.2387 | 43.5228 | 43.7895 | 44.0396 | 44.2741 | 44.494 | 44.7 | 44.893 | 45.0737 | 45.2429 | 45.4012 | 45.5493 | 45.6879 | 45.8175 | 45.9387 | 46.0519 | 46.1578 | 46.2568 | 46.3492 | 46.4356 | 46.5163 | 46.5917 | 46.6621 | 46.7278 | 46.7892 | 46.8465
Supercritical PC - Brown coal without CCS | 28.85 | 29.1217 | 29.38 | 29.6254 | 29.8584 | 30.0796 | 30.2895 | 30.4885 | 30.6772 | 30.8559 | 31.0253 | 31.1856 | 31.3374 | 31.4811 | 31.617 | 31.7455 | 31.8671 | 31.982 | 32.0906 | 32.1932 | 32.2902 | 32.3818 | 32.4683 | 32.55 | 32.6271 | 32.6999 | 32.7686 | 32.8335 | 32.8946 | 32.9524 | 33.0069
Wind - (100 MW) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Wave/Ocean | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100

## New Capital Costs
Capital Costs for New Technologies (2014-15 $/kW) |  | Year Ending June
Technology | Scenario | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Biomass | High | 5199.8744 | 5148.984 | 5065.0173 | 5032.1463 | 5117.9687 | 5163.7982 | 5162.6535 | 5156.4889 | 5148.5835 | 5142.632 | 5140.0417 | 5139.6321 | 5141.076 | 5146.3569 | 5153.9334 | 5161.7202 | 5170.8847 | 5182.3282 | 5196.0641 | 5211.7141 | 5229.0999 | 5247.9671 | 5268.1833 | 5289.5345 | 5311.7432 | 5331.3618 | 5352.8627 | 5374.0929 | 5394.99 | 5415.7775 | 5437.1046
Biomass | Medium | 5200 | 5157.6275 | 5088.661 | 5055.1388 | 5103.5688 | 5143.3179 | 5147.7764 | 5144.6831 | 5138.5807 | 5133.5133 | 5131.2601 | 5130.9953 | 5132.5573 | 5137.7981 | 5145.4181 | 5153.0179 | 5161.5846 | 5172.0168 | 5184.3634 | 5198.2437 | 5213.3583 | 5229.4181 | 5246.256 | 5263.7113 | 5281.5991 | 5298.101 | 5315.6298 | 5333.0006 | 5350.1911 | 5367.3294 | 5384.7558
Biomass | Low | 5203.4778 | 5169.3904 | 5114.0119 | 5043.903 | 4974.1918 | 4989.3246 | 4994.0187 | 4989.6519 | 4981.9718 | 4974.9422 | 4970.2849 | 4967.3958 | 4966.3168 | 4968.8618 | 4973.8663 | 4978.7278 | 4984.2768 | 4991.3672 | 5000.0334 | 5009.861 | 5020.4583 | 5031.5048 | 5042.8115 | 5054.2513 | 5065.7002 | 5076.9143 | 5088.3488 | 5099.7265 | 5111.0679 | 5122.4158 | 5133.8113
CCGT - With CCS | High | 2937.8018 | 2985.6266 | 2979.9145 | 2997.761 | 3110.1617 | 3169.8855 | 3169.8212 | 3160.4773 | 3145.4515 | 3131.3736 | 3121.776 | 3115.4221 | 3111.5923 | 3112.3801 | 3116.3407 | 3120.1062 | 3125.0776 | 3132.6725 | 3143.1957 | 3156.2983 | 3171.5527 | 3188.5841 | 3207.1297 | 3226.9892 | 3247.9312 | 3265.786 | 3285.8456 | 3305.6049 | 3324.9751 | 3344.2006 | 3364.0701
CCGT - With CCS | Medium | 2940.4 | 3006.3365 | 3026.7167 | 3047.1558 | 3109.5635 | 3161.4088 | 3167.0256 | 3160.6665 | 3147.9869 | 3135.38 | 3126.306 | 3119.9424 | 3115.9589 | 3116.5254 | 3120.3258 | 3123.7078 | 3127.8909 | 3134.2357 | 3143.0034 | 3153.7813 | 3166.0229 | 3179.3081 | 3193.3463 | 3207.9753 | 3223.0356 | 3236.7454 | 3251.4513 | 3266.0048 | 3280.385 | 3294.7119 | 3309.3196
CCGT - With CCS | Low | 2946.7689 | 3030.8096 | 3073.7487 | 3086.674 | 3086.416 | 3125.2649 | 3132.0672 | 3125.3627 | 3112.6296 | 3099.7507 | 3089.7648 | 3082.0864 | 3076.742 | 3075.9956 | 3078.5923 | 3080.684 | 3083.3179 | 3087.7654 | 3094.2148 | 3102.1721 | 3110.9926 | 3120.2157 | 3129.5328 | 3138.8082 | 3147.936 | 3157.2409 | 3166.4828 | 3175.6999 | 3184.9326 | 3194.1941 | 3203.4169
CCGT - Without CCS | High | 1091.158 | 1105.071 | 1102.2813 | 1107.3424 | 1142.8151 | 1161.4167 | 1160.5961 | 1157.2086 | 1152.512 | 1148.34 | 1145.5507 | 1143.6985 | 1142.5987 | 1142.9996 | 1144.3472 | 1145.6688 | 1147.4323 | 1150.0517 | 1153.5777 | 1157.8747 | 1162.8373 | 1168.3524 | 1174.35 | 1180.7527 | 1187.4647 | 1193.248 | 1199.7053 | 1206.0659 | 1212.3075 | 1218.5093 | 1224.9046
CCGT - Without CCS | Medium | 1091.6 | 1110.2393 | 1114.8037 | 1120.1512 | 1139.7437 | 1155.8004 | 1157.0605 | 1154.7912 | 1150.8466 | 1147.0935 | 1144.4559 | 1142.629 | 1141.5258 | 1141.8794 | 1143.2072 | 1144.4248 | 1145.9331 | 1148.1363 | 1151.0854 | 1154.6342 | 1158.6328 | 1162.9532 | 1167.5139 | 1172.2549 | 1177.1113 | 1181.5709 | 1186.3307 | 1191.0411 | 1195.6993 | 1200.3446 | 1205.0721
CCGT - Without CCS | Low | 1093.3417 | 1116.6072 | 1127.62 | 1129.5994 | 1127.667 | 1139.2822 | 1141.0681 | 1138.766 | 1134.7741 | 1130.8622 | 1127.8758 | 1125.5944 | 1124.0306 | 1123.9252 | 1124.8331 | 1125.5956 | 1126.5534 | 1128.0876 | 1130.2348 | 1132.8288 | 1135.6845 | 1138.6611 | 1141.6694 | 1144.6609 | 1147.592 | 1150.598 | 1153.5752 | 1156.5436 | 1159.5185 | 1162.5051 | 1165.4754
Integrated Solar Combined Cycle (ISCS) | High | 2149.1376 | 2167.6231 | 2153.4726 | 2154.9413 | 2216.2621 | 2244.5459 | 2234.9337 | 2220.3562 | 2203.1957 | 2187.0936 | 2173.8163 | 2162.5156 | 2152.8145 | 2146.1328 | 2141.434 | 2136.7586 | 2133.0001 | 2130.9835 | 2130.836 | 2132.3118 | 2135.1825 | 2139.2216 | 2144.2795 | 2150.2159 | 2156.8644 | 2161.4602 | 2167.5269 | 2173.3911 | 2178.9956 | 2184.5056 | 2190.4438
Integrated Solar Combined Cycle (ISCS) | Medium | 2150 | 2177.8628 | 2178.3266 | 2180.5257 | 2210.7532 | 2234.1782 | 2228.7087 | 2216.3891 | 2200.8077 | 2185.6503 | 2172.7808 | 2161.6194 | 2151.9886 | 2145.2989 | 2140.6379 | 2135.8404 | 2131.677 | 2128.9507 | 2127.7809 | 2127.8937 | 2128.9788 | 2130.7815 | 2133.1325 | 2135.9207 | 2139.0326 | 2141.1433 | 2143.9892 | 2146.7245 | 2149.3313 | 2151.8978 | 2154.6726
Integrated Solar Combined Cycle (ISCS) | Low | 2153.4305 | 2190.4634 | 2203.7381 | 2199.5454 | 2187.9412 | 2202.9586 | 2198.7336 | 2186.5678 | 2171.1404 | 2155.9347 | 2142.6419 | 2130.8422 | 2120.5574 | 2113.2243 | 2107.9952 | 2102.5662 | 2097.5949 | 2093.8374 | 2091.3795 | 2089.9037 | 2089.0342 | 2088.4912 | 2088.0924 | 2087.7465 | 2087.3776 | 2086.931 | 2086.5772 | 2086.1911 | 2085.7913 | 2085.3999 | 2085.0237
Large Scale Battery Storage | High | 4498.1951 | 4546.187 | 4525.5627 | 4537.4244 | 4674.5632 | 4742.3135 | 4730.3362 | 4707.8332 | 4679.8895 | 4654.0957 | 4634.0714 | 4618.0121 | 4605.143 | 4598.4915 | 4595.8334 | 4593.1124 | 4592.2273 | 4594.896 | 4601.3573 | 4611.0764 | 4623.5969 | 4638.4484 | 4655.3308 | 4673.9388 | 4693.9024 | 4709.8739 | 4728.7257 | 4747.1718 | 4765.1093 | 4782.8701 | 4801.4629
Large Scale Battery Storage | Medium | 4500 | 4567.5559 | 4577.3848 | 4590.6027 | 4662.4727 | 4719.8959 | 4716.545 | 4698.7129 | 4673.9754 | 4650.0388 | 4630.7591 | 4614.903 | 4602.1058 | 4595.3544 | 4592.701 | 4589.6447 | 4587.8176 | 4588.8944 | 4593.1062 | 4599.8665 | 4608.5416 | 4618.6017 | 4629.7019 | 4641.603 | 4654.0539 | 4664.7082 | 4676.7032 | 4688.4863 | 4700.0357 | 4711.52 | 4723.3775
Large Scale Battery Storage | Low | 4507.1801 | 4593.8682 | 4630.3959 | 4629.9847 | 4613.717 | 4653.1933 | 4652.235 | 4634.5039 | 4609.8395 | 4585.5357 | 4565.1064 | 4547.6587 | 4533.2423 | 4524.8872 | 4520.7913 | 4516.1548 | 4512.3681 | 4511.0091 | 4512.2438 | 4515.3992 | 4519.7002 | 4524.5644 | 4529.6177 | 4534.6653 | 4539.5389 | 4544.5508 | 4549.5556 | 4554.514 | 4559.4792 | 4564.4808 | 4569.4512
OCGT - Without CCS | High | 723.7738 | 738.4091 | 737.5642 | 743.2231 | 775.6524 | 793.163 | 793.9406 | 791.7881 | 787.6481 | 783.6141 | 780.8884 | 779.1571 | 778.1824 | 778.5007 | 779.7693 | 780.9564 | 782.4453 | 784.6671 | 787.7422 | 791.5891 | 796.0635 | 801.0544 | 806.4768 | 812.2836 | 818.4249 | 823.6463 | 829.5168 | 835.3024 | 840.9737 | 846.5989 | 852.4163
OCGT - Without CCS | Medium | 724.8 | 745.3677 | 752.6581 | 759.4535 | 777.6224 | 792.9138 | 795.1033 | 793.6728 | 790.1938 | 786.6117 | 784.0429 | 782.2847 | 781.2297 | 781.4648 | 782.6618 | 783.7235 | 784.9879 | 786.8638 | 789.4488 | 792.6362 | 796.2529 | 800.1749 | 804.3116 | 808.6227 | 813.073 | 817.1134 | 821.4507 | 825.745 | 829.9876 | 834.2122 | 838.5221
OCGT - Without CCS | Low | 726.8267 | 753.3969 | 767.6538 | 772.9856 | 774.3666 | 786.1545 | 788.5641 | 786.9709 | 783.4917 | 779.878 | 777.0852 | 774.9715 | 773.5415 | 773.4253 | 774.2986 | 775.0175 | 775.8746 | 777.2495 | 779.2128 | 781.63 | 784.3029 | 787.0962 | 789.9153 | 792.7255 | 795.5036 | 798.3179 | 801.1212 | 803.918 | 806.718 | 809.5244 | 812.3228
Pumped Hydro Storage | High | 3201.2062 | 3169.9777 | 3123.7991 | 3105.8669 | 3150.416 | 3174.9751 | 3175.1524 | 3174.1227 | 3173.8741 | 3175.3378 | 3178.3483 | 3182.1548 | 3186.7406 | 3193.3519 | 3200.9227 | 3208.7487 | 3217.4798 | 3227.4404 | 3238.4863 | 3250.351 | 3263.0481 | 3276.4727 | 3290.606 | 3305.2982 | 3320.3391 | 3334.1751 | 3348.9196 | 3363.5188 | 3377.9566 | 3392.3555 | 3407.0045
Pumped Hydro Storage | Medium | 3200 | 3169.6607 | 3127.7982 | 3107.8009 | 3134.0424 | 3155.4743 | 3159.2747 | 3160.2878 | 3160.9305 | 3162.6567 | 3165.7713 | 3169.7286 | 3174.508 | 3181.1624 | 3188.844 | 3196.6247 | 3205.0344 | 3214.4239 | 3224.7127 | 3235.6649 | 3247.2123 | 3259.232 | 3271.6787 | 3284.4461 | 3297.3968 | 3309.6682 | 3322.4615 | 3335.1666 | 3347.7795 | 3360.3737 | 3373.1086
Pumped Hydro Storage | Low | 3200.8009 | 3170.902 | 3133.3772 | 3090.4637 | 3049.1135 | 3056.4008 | 3060.5641 | 3060.9637 | 3060.492 | 3060.7733 | 3062.2637 | 3064.5557 | 3067.684 | 3072.6092 | 3078.61 | 3084.6184 | 3091.0692 | 3098.3081 | 3106.2758 | 3114.7394 | 3123.5721 | 3132.6352 | 3141.8663 | 3151.1853 | 3160.4992 | 3169.673 | 3178.9844 | 3188.2588 | 3197.5097 | 3206.767 | 3216.0526
Solar PV SAT | High | 2896.8661 | 2920.8347 | 2894.0105 | 2892.1395 | 2995.0277 | 3047.997 | 3044.3791 | 3030.6335 | 3013.8802 | 3001.3521 | 2993.4306 | 2988.9446 | 2987.0862 | 2989.851 | 2995.924 | 3001.7159 | 3008.6183 | 3018.1359 | 3030.6536 | 3049.6904 | 3070.9592 | 3094.0695 | 3118.7337 | 3144.7689 | 3171.9715 | 3195.9178 | 3222.1726 | 3248.1209 | 3273.6619 | 3299.0441 | 3325.106
Solar PV SAT | Medium | 2900 | 2943.9064 | 2945.1648 | 2946.9452 | 2999.0481 | 3044.1746 | 3045.9454 | 3035.0095 | 3020.6462 | 3009.6682 | 3002.2759 | 2997.7046 | 2995.5874 | 2998.0625 | 3003.8959 | 3009.243 | 3015.3255 | 3023.5756 | 3034.3111 | 3050.9274 | 3069.0692 | 3088.2997 | 3108.3073 | 3128.9396 | 3150.0547 | 3169.7174 | 3190.4386 | 3211.0037 | 3231.3844 | 3251.7034 | 3272.3248
Solar PV SAT | Low | 2906.8649 | 2970.824 | 2996.2486 | 2991.0448 | 2979.7449 | 3011.9317 | 3014.7845 | 3003.4909 | 2989.1295 | 2977.8813 | 2969.5432 | 2963.5775 | 2960.0038 | 2961.0933 | 2965.6438 | 2969.6316 | 2974.1112 | 2980.4152 | 2988.7731 | 3002.3445 | 3016.8188 | 3031.7183 | 3046.715 | 3061.6794 | 3076.5177 | 3091.4975 | 3106.4339 | 3121.3455 | 3136.2693 | 3151.2181 | 3166.1358
Solar PV DAT | High | 3795.8935 | 3827.3006 | 3792.1516 | 3789.7001 | 3924.519 | 3993.9271 | 3989.1864 | 3971.1749 | 3949.2223 | 3932.8061 | 3922.4264 | 3916.5481 | 3914.113 | 3917.7358 | 3925.6936 | 3933.2829 | 3942.3274 | 3954.7987 | 3971.2013 | 3996.1461 | 4024.0155 | 4054.298 | 4086.6165 | 4120.7316 | 4156.3765 | 4187.7543 | 4222.1572 | 4256.1585 | 4289.6259 | 4322.8854 | 4357.0355
Solar PV DAT | Medium | 3800 | 3857.5326 | 3859.1814 | 3861.5144 | 3929.7872 | 3988.9185 | 3991.2388 | 3976.9089 | 3958.0881 | 3943.7032 | 3934.0167 | 3928.0268 | 3925.2525 | 3928.4958 | 3936.1395 | 3943.146 | 3951.1161 | 3961.9266 | 3975.9938 | 3997.767 | 4021.5389 | 4046.7376 | 4072.9544 | 4099.9898 | 4127.6579 | 4153.4228 | 4180.5747 | 4207.522 | 4234.2278 | 4260.8528 | 4287.8739
Solar PV DAT | Low | 3808.9953 | 3892.8038 | 3926.1188 | 3919.3001 | 3904.4933 | 3946.6691 | 3950.4072 | 3935.6088 | 3916.7904 | 3902.0514 | 3891.1256 | 3883.3084 | 3878.6257 | 3880.0532 | 3886.0159 | 3891.2414 | 3897.1112 | 3905.3716 | 3916.3233 | 3934.1066 | 3953.0729 | 3972.5964 | 3992.2473 | 4011.8558 | 4031.299 | 4050.9278 | 4070.4996 | 4090.0389 | 4109.5942 | 4129.1823 | 4148.7297
Solar PV FFP | High | 2347.4604 | 2366.8833 | 2345.1464 | 2343.6303 | 2427.0052 | 2469.9286 | 2466.9969 | 2455.8581 | 2442.2822 | 2432.1301 | 2425.711 | 2422.0758 | 2420.5699 | 2422.8103 | 2427.7316 | 2432.425 | 2438.0182 | 2445.7308 | 2455.8745 | 2471.3008 | 2488.5359 | 2507.2632 | 2527.2497 | 2548.3472 | 2570.3907 | 2589.7954 | 2611.0709 | 2632.098 | 2652.795 | 2673.3633 | 2694.4825
Solar PV FFP | Medium | 2350 | 2385.5794 | 2386.599 | 2388.0418 | 2430.2632 | 2466.8312 | 2468.2661 | 2459.4042 | 2447.765 | 2438.8691 | 2432.8788 | 2429.1745 | 2427.4588 | 2429.4645 | 2434.1915 | 2438.5245 | 2443.4534 | 2450.1388 | 2458.8383 | 2472.3032 | 2487.0043 | 2502.5877 | 2518.8007 | 2535.52 | 2552.6306 | 2568.5641 | 2585.3554 | 2602.0202 | 2618.5356 | 2635.0011 | 2651.7115
Solar PV FFP | Low | 2355.5629 | 2407.3918 | 2427.9945 | 2423.7777 | 2414.6209 | 2440.7033 | 2443.015 | 2433.8633 | 2422.2257 | 2413.1107 | 2406.354 | 2401.5197 | 2398.6238 | 2399.5066 | 2403.1941 | 2406.4256 | 2410.0556 | 2415.164 | 2421.9368 | 2432.9343 | 2444.6635 | 2456.7372 | 2468.8898 | 2481.0161 | 2493.0402 | 2505.179 | 2517.2826 | 2529.3661 | 2541.4596 | 2553.5733 | 2565.6618
Solar Thermal CLF | High | 4497.4027 | 4477.9681 | 4406.8205 | 4373.1229 | 4481.6778 | 4532.017 | 4515.1206 | 4486.7625 | 4460.4037 | 4444.2542 | 4433.7105 | 4427.1715 | 4423.761 | 4426.1883 | 4432.5557 | 4438.6818 | 4446.3547 | 4457.338 | 4471.9809 | 4499.1492 | 4529.0872 | 4561.3274 | 4595.5517 | 4631.4962 | 4668.8468 | 4702.1683 | 4738.3711 | 4774.1801 | 4809.4802 | 4844.5929 | 4880.546
Solar Thermal CLF | Medium | 4500 | 4502.0387 | 4462.9066 | 4432.2505 | 4477.9746 | 4518.624 | 4509.3379 | 4485.0629 | 4461.7492 | 4447.4088 | 4437.5047 | 4430.9654 | 4427.3868 | 4429.5443 | 4435.7259 | 4441.3749 | 4448.0429 | 4457.4276 | 4469.8346 | 4493.9634 | 4519.9935 | 4547.3996 | 4575.8254 | 4605.0596 | 4634.8871 | 4662.8672 | 4692.2068 | 4721.3403 | 4750.2366 | 4779.0592 | 4808.2662
Solar Thermal CLF | Low | 4507.5982 | 4530.9455 | 4519.6771 | 4473.5543 | 4426.7331 | 4448.9633 | 4441.639 | 4417.3253 | 4393.9536 | 4378.9374 | 4367.5564 | 4359.0458 | 4353.4418 | 4353.6212 | 4357.9638 | 4361.6568 | 4366.0294 | 4372.6707 | 4381.8007 | 4401.6503 | 4422.6297 | 4444.162 | 4465.866 | 4487.5664 | 4509.12 | 4530.7843 | 4552.4494 | 4574.0726 | 4595.7011 | 4617.3606 | 4638.9949
Solar Thermal CR WS | High | 6696.1329 | 6667.1969 | 6561.2661 | 6511.0941 | 6672.7203 | 6747.6698 | 6722.5129 | 6680.2908 | 6641.0455 | 6617.0006 | 6601.3024 | 6591.5664 | 6586.4887 | 6590.1026 | 6599.5829 | 6608.7041 | 6620.1281 | 6636.481 | 6658.2827 | 6698.7332 | 6743.3076 | 6791.3097 | 6842.2658 | 6895.7832 | 6951.3941 | 7001.0061 | 7054.9081 | 7108.2237 | 7160.7816 | 7213.0605 | 7266.5907
Solar Thermal CR WS | Medium | 6700 | 6703.0354 | 6644.772 | 6599.1285 | 6667.2067 | 6727.729 | 6713.9032 | 6677.7603 | 6643.0488 | 6621.6976 | 6606.9514 | 6597.2151 | 6591.887 | 6595.0993 | 6604.303 | 6612.7138 | 6622.6416 | 6636.6145 | 6655.087 | 6691.0122 | 6729.7682 | 6770.5727 | 6812.8956 | 6856.422 | 6900.8319 | 6942.4911 | 6986.1746 | 7029.5511 | 7072.5744 | 7115.4882 | 7158.9741
Solar Thermal CR WS | Low | 6711.3129 | 6746.0744 | 6729.2971 | 6660.6252 | 6590.9138 | 6624.012 | 6613.1069 | 6576.9065 | 6542.1087 | 6519.7513 | 6502.8062 | 6490.1348 | 6481.7911 | 6482.0582 | 6488.5239 | 6494.0223 | 6500.5327 | 6510.4208 | 6524.0143 | 6553.5682 | 6584.8042 | 6616.8634 | 6649.1783 | 6681.4878 | 6713.5786 | 6745.8345 | 6778.0913 | 6810.2859 | 6842.4883 | 6874.7369 | 6906.9479
Solar Thermal PT WS | High | 9096.2538 | 9076.5795 | 8949.3093 | 8889.3036 | 9107.0718 | 9205.4342 | 9165.0673 | 9102.7467 | 9046.2707 | 9011.3638 | 8987.7206 | 8971.8895 | 8962.2349 | 8964.5691 | 8974.693 | 8984.4079 | 8997.4379 | 9017.2557 | 9044.4164 | 9096.7487 | 9154.5965 | 9217.0239 | 9283.4267 | 9353.2185 | 9425.6795 | 9490.2972 | 9560.569 | 9630.0472 | 9698.5264 | 9766.657 | 9836.4224
Solar Thermal PT WS | Medium | 9100 | 9120.2483 | 9054.9881 | 8999.4087 | 9088.9797 | 9167.5758 | 9143.8733 | 9090.6125 | 9040.4506 | 9009.0991 | 8986.7389 | 8971.0327 | 8961.2176 | 8963.1065 | 8972.9835 | 8981.8112 | 8992.7993 | 9009.3154 | 9031.8731 | 9077.9491 | 9127.7759 | 9180.2984 | 9234.8253 | 9290.8943 | 9348.0163 | 9401.6851 | 9457.9332 | 9513.7728 | 9569.1625 | 9624.428 | 9680.4108
Solar Thermal PT WS | Low | 9114.3727 | 9173.7331 | 9162.7677 | 9080.1975 | 8993.9896 | 9037.7225 | 9018.8962 | 8966.1496 | 8916.1498 | 8883.6301 | 8858.52 | 8839.1385 | 8825.5736 | 8823.7689 | 8830.259 | 8835.4399 | 8842.0506 | 8853.2552 | 8869.4229 | 8907.191 | 8947.1564 | 8988.1589 | 9029.4499 | 9070.651 | 9111.4348 | 9152.6849 | 9193.787 | 9234.814 | 9275.8778 | 9317.0242 | 9358.0684
Supercritical PC - Black coal with CCS | High | 5388.4732 | 5373.9077 | 5310.178 | 5287.1864 | 5383.055 | 5423.9087 | 5399.9282 | 5370.0871 | 5338.9939 | 5310.987 | 5287.3851 | 5266.4803 | 5247.92 | 5234.5364 | 5224.0599 | 5213.8494 | 5205.5085 | 5200.1763 | 5197.7879 | 5197.7941 | 5200.0008 | 5204.0703 | 5209.8386 | 5216.9943 | 5225.1339 | 5230.1647 | 5237.4857 | 5244.4628 | 5251.0349 | 5257.4864 | 5264.5847
Supercritical PC - Black coal with CCS | Medium | 5387.55 | 5382.1337 | 5336.7013 | 5311.6636 | 5356.5856 | 5389.2388 | 5373.7352 | 5348.6402 | 5320.1929 | 5293.4627 | 5270.4608 | 5249.9757 | 5231.8241 | 5218.5869 | 5208.3802 | 5198.0989 | 5189.0893 | 5182.5051 | 5178.3532 | 5176.0954 | 5175.3631 | 5175.7714 | 5177.1067 | 5179.1368 | 5181.5927 | 5182.5415 | 5184.6377 | 5186.5432 | 5188.2477 | 5189.906 | 5191.8769
Supercritical PC - Black coal with CCS | Low | 5391.4972 | 5394.3692 | 5365.6638 | 5313.7184 | 5255.0682 | 5266.9247 | 5254.0302 | 5229.3196 | 5200.6141 | 5173.0396 | 5148.6557 | 5126.5666 | 5106.8348 | 5091.9493 | 5080.2433 | 5068.3115 | 5057.2827 | 5048.2637 | 5041.2582 | 5035.6919 | 5031.0652 | 5026.9512 | 5023.1047 | 5019.3437 | 5015.4865 | 5011.5608 | 5007.7696 | 5003.9172 | 5000.0446 | 4996.1975 | 4992.3625
Supercritical PC - Black coal without CCS | High | 2880.4793 | 2882.0357 | 2853.7191 | 2846.1698 | 2904.2627 | 2929.8782 | 2917.3844 | 2901.1995 | 2883.9885 | 2868.463 | 2855.5414 | 2844.2412 | 2834.3307 | 2827.4409 | 2822.2791 | 2817.2357 | 2813.2477 | 2811.0071 | 2810.4987 | 2811.41 | 2813.6114 | 2816.9006 | 2821.1743 | 2826.255 | 2831.9147 | 2835.7595 | 2840.9383 | 2845.9181 | 2850.662 | 2855.3345 | 2860.3846
Supercritical PC - Black coal without CCS | Medium | 2880.15 | 2887.6892 | 2870.7079 | 2862.2367 | 2890.1857 | 2910.9622 | 2903.3218 | 2889.8427 | 2874.1839 | 2859.4299 | 2846.8615 | 2835.7854 | 2826.0839 | 2819.2598 | 2814.2329 | 2809.1299 | 2804.74 | 2801.7595 | 2800.2084 | 2799.7759 | 2800.2326 | 2801.3482 | 2802.9915 | 2805.0293 | 2807.3093 | 2808.7325 | 2810.8081 | 2812.7751 | 2814.628 | 2816.4546 | 2818.4589
Supercritical PC - Black coal without CCS | Low | 2882.6348 | 2895.6842 | 2888.9719 | 2867.6353 | 2841.243 | 2851.1025 | 2844.9902 | 2831.7636 | 2816.0345 | 2800.8863 | 2787.5998 | 2775.6637 | 2765.1126 | 2757.4069 | 2751.585 | 2745.6021 | 2740.1215 | 2735.8092 | 2732.6791 | 2730.396 | 2728.655 | 2727.2011 | 2725.8849 | 2724.6017 | 2723.2488 | 2721.8947 | 2720.5916 | 2719.2563 | 2717.9142 | 2716.5889 | 2715.2624
Supercritical PC - Brown coal with CCS | High | 8278.5684 | 8256.1907 | 8158.2797 | 8122.9565 | 8270.2442 | 8333.0096 | 8296.1672 | 8250.321 | 8202.5509 | 8159.5227 | 8123.2618 | 8091.1449 | 8062.6298 | 8042.0679 | 8025.9723 | 8010.2856 | 7997.4709 | 7989.2788 | 7985.6094 | 7985.6189 | 7989.0092 | 7995.2613 | 8004.1234 | 8015.1172 | 8027.6225 | 8035.3515 | 8046.599 | 8057.3183 | 8067.4153 | 8077.3271 | 8088.2325
Supercritical PC - Brown coal with CCS | Medium | 8277.15 | 8268.8286 | 8199.0287 | 8160.5621 | 8229.5779 | 8279.7446 | 8255.9257 | 8217.371 | 8173.666 | 8132.5992 | 8097.2603 | 8065.7881 | 8037.9009 | 8017.564 | 8001.8828 | 7986.0873 | 7972.2454 | 7962.1298 | 7955.7509 | 7952.2821 | 7951.1571 | 7951.7845 | 7953.8359 | 7956.9548 | 7960.728 | 7962.1857 | 7965.4062 | 7968.3336 | 7970.9524 | 7973.5002 | 7976.5281
Supercritical PC - Brown coal with CCS | Low | 8283.2143 | 8287.6266 | 8243.5253 | 8163.7189 | 8073.6118 | 8091.8276 | 8072.0172 | 8034.0531 | 7989.9514 | 7947.5875 | 7910.1252 | 7876.1888 | 7845.8739 | 7823.0046 | 7805.02 | 7786.6887 | 7769.7446 | 7755.8883 | 7745.1254 | 7736.5736 | 7729.4653 | 7723.1449 | 7717.2353 | 7711.4571 | 7705.5311 | 7699.4998 | 7693.6753 | 7687.7566 | 7681.807 | 7675.8965 | 7670.0046
Supercritical PC - Brown coal without CCS | High | 4386.3051 | 4383.6581 | 4337.0558 | 4323.0608 | 4409.0024 | 4446.8075 | 4428.1346 | 4403.96 | 4378.2286 | 4354.9866 | 4335.6191 | 4318.6736 | 4303.8023 | 4293.4183 | 4285.6118 | 4277.9867 | 4271.931 | 4268.4746 | 4267.5986 | 4268.8415 | 4272.0082 | 4276.7983 | 4283.0573 | 4290.5231 | 4298.8591 | 4304.4771 | 4312.0908 | 4319.4078 | 4326.372 | 4333.2283 | 4340.6502
Supercritical PC - Brown coal without CCS | Medium | 4385.85 | 4392.1608 | 4362.4432 | 4347.1256 | 4388.3725 | 4419.0048 | 4407.5032 | 4387.3249 | 4363.8929 | 4341.7972 | 4322.9533 | 4306.3362 | 4291.7699 | 4281.4802 | 4273.8698 | 4266.1535 | 4259.5011 | 4254.9478 | 4252.5259 | 4251.7756 | 4252.3546 | 4253.9208 | 4256.2784 | 4259.2309 | 4262.5533 | 4264.5799 | 4267.5906 | 4270.4387 | 4273.1145 | 4275.7497 | 4278.6537
Supercritical PC - Brown coal without CCS | Low | 4389.563 | 4404.1511 | 4389.7292 | 4353.9215 | 4311.1358 | 4324.8705 | 4315.5672 | 4295.7018 | 4272.1133 | 4249.384 | 4229.4239 | 4211.4778 | 4195.5965 | 4183.9447 | 4175.0996 | 4166.0229 | 4157.6978 | 4151.1143 | 4146.2945 | 4142.7424 | 4140.0035 | 4137.6995 | 4135.6079 | 4133.5739 | 4131.4456 | 4129.2936 | 4127.2319 | 4125.1209 | 4122.9973 | 4120.8971 | 4118.7999
Wind Onshore - (100 MW) | High | 2547.1294 | 2590.0681 | 2576.3937 | 2581.3434 | 2673.9453 | 2721.7536 | 2718.5126 | 2709.4279 | 2697.5302 | 2689.2955 | 2685.2469 | 2678.0216 | 2676.3375 | 2678.8536 | 2684.3722 | 2689.6537 | 2695.9594 | 2704.6482 | 2716.0644 | 2733.0195 | 2751.9872 | 2772.6148 | 2794.6429 | 2817.9048 | 2842.2142 | 2863.596 | 2887.0546 | 2910.2369 | 2933.0526 | 2955.7262 | 2979.0108
Wind Onshore - (100 MW) | Medium | 2550 | 2610.9505 | 2622.6087 | 2630.7916 | 2677.4616 | 2718.1819 | 2719.8306 | 2713.2572 | 2703.4845 | 2696.6104 | 2693.0003 | 2685.7387 | 2683.8234 | 2686.0784 | 2691.3816 | 2696.2608 | 2701.8226 | 2709.3608 | 2719.1604 | 2733.9235 | 2750.06 | 2767.1753 | 2784.9879 | 2803.3593 | 2822.1597 | 2839.6634 | 2858.1136 | 2876.4234 | 2894.5685 | 2912.659 | 2931.0194
Wind Onshore - (100 MW) | Low | 2556.23 | 2635.3042 | 2668.7555 | 2671.0845 | 2661.6459 | 2690.913 | 2693.5624 | 2686.5798 | 2676.7249 | 2669.5273 | 2664.9806 | 2656.5831 | 2653.3735 | 2654.397 | 2658.5619 | 2662.2326 | 2666.3641 | 2672.1604 | 2679.8272 | 2691.8726 | 2704.729 | 2717.9647 | 2731.2836 | 2744.5679 | 2757.7315 | 2771.0378 | 2784.2953 | 2797.5312 | 2810.7799 | 2824.0522 | 2837.2933
Wave/Ocean | High | 5901.5592 | 5792.8718 | 5651.5898 | 5563.0544 | 5595.6056 | 5584.9639 | 5522.9963 | 5457.8721 | 5393.2534 | 5332.1286 | 5275.2102 | 5221.0927 | 5169.5365 | 5122.8247 | 5079.082 | 5036.2586 | 4995.6 | 4957.9619 | 4923.2627 | 4891.0575 | 4861.1872 | 4833.3739 | 4807.4736 | 4783.2314 | 4760.3295 | 4733.5618 | 4709.5636 | 4685.1851 | 4660.3167 | 4635.2706 | 4611.0308
Wave/Ocean | Medium | 5900 | 5796.6066 | 5668.3232 | 5577.4907 | 5569.8865 | 5553.045 | 5498.5589 | 5437.7396 | 5375.5212 | 5315.6447 | 5259.474 | 5205.9935 | 5155.0653 | 5108.7453 | 5065.485 | 5022.8587 | 4981.9116 | 4943.5207 | 4907.6679 | 4873.9187 | 4841.9759 | 4811.5256 | 4782.3858 | 4754.364 | 4727.2441 | 4697.5115 | 4669.6552 | 4641.538 | 4613.0903 | 4584.5235 | 4556.5014
Wave/Ocean | Low | 5902.5969 | 5803.7045 | 5687.6655 | 5559.9767 | 5434.9515 | 5395.8422 | 5344.6662 | 5285.2546 | 5223.7882 | 5164.1524 | 5107.8122 | 5054.0062 | 5002.7752 | 4956.0855 | 4912.5741 | 4869.5738 | 4827.9586 | 4788.5737 | 4751.4019 | 4715.9812 | 4681.9111 | 4648.8453 | 4616.5783 | 4584.9564 | 4553.8306 | 4521.2094 | 4489.6781 | 4457.9863 | 4426.1044 | 4394.1591 | 4362.5252

## CO2 Storage Costs
CO2-e Transport and Storage Costs (2014-15 $/tonne)
Zone | Cost
NQ | 60
CQ | 60
SEQ | 25
SWQ | 25
NNS | 100
NCEN | 100
SWNSW | 40
CAN | 40
NVIC | 10
CVIC | 10
MEL | 10
LV | 10
TAS | 10
SESA | 10
ADE | 10
NSA | 10

## Build Limits
Build Limits by Technology
Technology | Region | Zone | Project lead time (Yrs) | Max Build Limit per Zone (MW) | Max Build Rate (MW/year)
Biomass | QLD | NQ | 8 | 400 | 100
Biomass | NSW | NCEN | 4 | 100 | 25
Biomass | NSW | CAN | 4 | 100 | 25
Biomass | NSW | NNS | 4 | 100 | 25
Biomass | SA | SESA | 4 | 300 | 50
Biomass | VIC | NVIC | 4 | 100 | 25
Biomass | TAS | TAS | 6 | 100 | 25
CCGT - With CCS | QLD | NQ, CQ, SWQ, SEQ | 8 |  | 800
CCGT - With CCS | NSW | NNS, NCEN | 8 |  | 800
CCGT - With CCS | VIC | LV | 8 |  | 800
CCGT - Without CCS | QLD | NQ, CQ, SWQ, SEQ | 4 |  | 800
CCGT - Without CCS | NSW | NNS, NCEN | 4 |  | 800
CCGT - Without CCS | VIC | LV | 4 |  | 800
CCGT - Without CCS | SA | SESA | 4 |  | 500
CCGT - Without CCS | TAS | TAS | 4 |  | 500
Integrated Solar Combined Cycle (ISCS) | NEM Wide |  |  |  | 100
Integrated Solar Combined Cycle (ISCS) | QLD | SWQ, CQ, NQ | 6 | 200 | 100
Integrated Solar Combined Cycle (ISCS) | NSW | NCEN, CAN | 6 | 200 | 100
Integrated Solar Combined Cycle (ISCS) | VIC | NVIC, CVIC | 6 | 200 | 100
Integrated Solar Combined Cycle (ISCS) | SA | NSA | 6 | 200 | 100
Large Scale Battery Storage | NEM Wide |  | 3 | 100 | 20
OCGT - Without CCS | QLD | All | 4 |  | 600
OCGT - Without CCS | NSW | All | 4 |  | 600
OCGT - Without CCS | VIC | All | 4 |  | 600
OCGT - Without CCS | SA | All | 4 |  | 300
OCGT - Without CCS | TAS | TAS | 4 |  | 300
Pumped Hydro Storage | QLD | All | 8 | 500 | 100
Pumped Hydro Storage | NSW | CAN | 8 | 500 | 100
Pumped Hydro Storage | VIC | NVIC | 8 | 500 | 100
Pumped Hydro Storage | SA | SESA | 8 | 300 | 100
Pumped Hydro Storage | TAS | TAS | 8 | 200 | 100
CLF, PV FFP, PV SAT CR S, PT S | NSW | CAN | 4 | 4000 | 200
CLF, PV FFP, PV SAT CR S, PT S | NSW | NCEN | 4 | 4000 | 200
CLF, PV FFP, PV SAT CR S, PT S | NSW | NNS | 4 | 4000 | 200
CLF, PV FFP, PV SAT CR S, PT S | QLD | NQ | 4 | 4000 | 200
CLF, PV FFP, PV SAT CR S, PT S | QLD | CQ | 4 | 4000 | 200
CLF, PV FFP, PV SAT CR S, PT S | QLD | SEQ | 4 | 4000 | 200
CLF, PV FFP, PV SAT CR S, PT S | QLD | SWQ | 4 | 4000 | 200
CLF, PV FFP, PV SAT CR S, PT S | VIC | CVIC | 4 | 4000 | 200
CLF, PV FFP, PV SAT CR S, PT S | SA | NSA | 4 | 4000 | 200
Solar PV DAT | N/A | N/A | N/A | N/A | N/A
Supercritical PC - Black coal with CCS | QLD | NQ, CQ, SWQ, SEQ | 8 |  | 800
Supercritical PC - Black coal with CCS | NSW | NNS | 8 |  | 800
Supercritical PC - Brown coal with CCS | VIC | LV | 8 |  | 1000
Wind - (100 MW) | NSW | NCEN | 4 | 1000 | 500
Wind - (100 MW) | NSW | NNS | 4 | 1000 | 500
Wind - (100 MW) | NSW | SWNSW | 4 | 1500 | 500
Wind - (100 MW) | NSW | CAN | 4 | 2000 | 500
Wind - (100 MW) | QLD | NQ | 4 | 500 | 200
Wind - (100 MW) | QLD | SWQ | 4 | 1000 | 200
Wind - (100 MW) | VIC | CVIC | 4 | 2000 | 100
Wind - (100 MW) | VIC | LV | 4 | 500 | 100
Wind - (100 MW) | VIC | MEL | 4 | 500 | 100
Wind - (100 MW) | SA | NSA | 4 | 1000 | 500
Wind - (100 MW) | SA | SESA | 4 | 500 | 500
Wind - (100 MW) | TAS | TAS | 4 | 1500 | 500
Wave/Ocean | VIC | CVIC | 4 | 100 | 20
Wave/Ocean | SA | SESA | 4 | 100 | 20
Wave/Ocean | TAS | TAS | 4 | 100 | 20
Supercritical PC - Black coal without CCS | QLD | All | 8 |  | 800
Supercritical PC - Black coal without CCS | NSW | NNS | 8 |  | 800
Supercritical PC - Brown coal without CCS | VIC | LV | 8 |  | 1000

## New Connection Costs
Connection Costs ($M/MW, 2014-15 $)
Technology | ADE | CAN | CQ | CVIC | LV | MEL | NCEN | NNS | NQ | NSA | NVIC | SEQ | SESA | SWNSW | SWQ | TAS
Biomass |  | 0.1 |  |  |  |  | 0.1 | 0.1 | 0.1 |  |  |  | 0.1 |  |  | 0.1
CCGT - With CCS | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 |  | 0.11 | 0.11
CCGT - Without CCS | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Integrated Solar Combined Cycle (ISCS) | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
Large Scale Battery Storage
OCGT - Without CCS | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Pumped Hydro Storage
Solar PV SAT
Solar PV DAT
Solar PV FFP | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
Solar Thermal CLF | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
Solar Thermal CR WS | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
Solar Thermal PT WS | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
Supercritical PC - Black coal oxy-combustion CCS |  |  | 0.13 |  |  |  | 0.13 | 0.13 | 0.13 |  |  | 0.13 |  | 0.13 | 0.13
Supercritical PC - Black coal with CCS |  |  | 0.13 |  |  |  | 0.13 | 0.13 | 0.13 |  |  | 0.13 |  | 0.13 | 0.13
Supercritical PC - Brown coal with CCS |  |  |  |  | 0.13
Wind - (100 MW) | 0.14 | 0.14 |  | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 |  |  | 0.14 | 0.14 | 0.14 | 0.14
Wave/Ocean
Supercritical PC - Black coal without CCS |  |  | 0.13 |  |  |  | 0.13 | 0.13 | 0.13 |  |  | 0.13 |  | 0.13 | 0.13
Supercritical PC - Brown coal without CCS |  |  |  |  | 0.13